## Instrument
ITEM# | PLANT | PART | SYS | SYS # | ISA ID | EQ | EQ # | COM. | Item Ref | TAG NUMBER | INSTRUMENT TYPE | PART OF PLANT | SYSTEM | Associated EquiP # | Associated Equip Description | Parameter | Line Number | LINE SIZE (mm) | LINE SPEC (Note 5) | Service | Press Min | Press Max | Temp. Min | Temp. Max | Flow Min | Flow max | UNITS | INSTRUMENT RANGE | OPERATING VALUE | CALIBRATED RANGE | INSTALLATION DRAWING (TABG-JEC-0-000-) | DATASHEET / Reference (TABG-JEC-0-000-) | P&ID (TABG-JEC-0-000-) | NOTES | REV | VENDOR | MAKE | MODEL | PO | RCVD | FailSafe
261 | TH00 | 011 | 0LFC | 10 | LIT | CL | 010 |  | 38 | 0110LFC10CL010 | Level Transmitter (Radar) | Wellpad TH11 | Common Steam/Water Dump System | - | Wellpad Pond | Level | N/A | N/A | CL1 | LP Two Phase | atm | atm | -5 | 100 | - | - | mm | 2200 to 6000 | - | 2200 to 6000 | CCI-DET-2706 CCI-DET-2711 | CCI-DAT-1468 | PRO-PID-0033 | Bracket Mount | 7.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
257 | TH00 | 011 | 0NAB | 10 | FIT | DF | 010 |  | 34 | 0110NAB10CF010 | Flow Transmitter (Orifice Flow) | Wellpad TH11 | Condensate System | - | Well TH11 | Flow | 0110NAB10-BR010-300-S12 | 300 | S12 | Condensate | Full Vac | 23 | -5 | 215 | 0 | 1399 | tph | -10 to 1399 | 550 | 0 to 1399T/H 0 to 621.3mb | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0033 | Notes 3, Note 4, Note 8 | 7.8 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ | 4500191995 | 2023-02-13
260 | TH00 | 011 | 0NAB | 10 | PIT | CP | 010 |  | 37 | 0110NAB10CP010 | Pressure Indicating Transmitter | Wellpad TH11 | Condensate System | - | Well TH11 | Pressure | N/A | 3 1/8" | S12 | Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 5.1 | 0 to 25 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0033 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
259 | TH00 | 011 | 0NAB | 10 | PI | CP | 510 |  | 36 | 0110NAB10CP510 | Pressure Gauge | Wellpad TH11 | Condensate System | - | Well TH11 | Pressure | N/A | 3 1/8" | S12 | Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | 0 to 25 | 5.1 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0033 |  | 3.2 | Wika | Wika | 72039878+14503369+0731277 | 4500189704 | 2022-11-10
258 | TH00 | 011 | 0NAB | 10 | PI | CP | 520 |  | 35 | 0110NAB10CP520 | Pressure Gauge | Wellpad TH11 | Condensate System | - | Well TH11 FCV Inlet | Pressure | 0110NAB10-BR010-300-S12 | 300 | S12 | Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | 0 to 60 | 5.1 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0033 |  | 7.3 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
299 | TH00 | 012 | 0LFC | 10 | LIT | CL | 010 |  | 80 | 0120LFC10CL010 | Level Transmitter (Radar) | Wellpad TH12 | Common Steam/Water Dump System | 0120LFC10-BB010 | Silencer | Level | N/A | N/A | CL1 | LP Two Phase | atm | atm | -5 | 100 | - | - | mm | 0 to 1300 | 950 | 0 to 1300 | (LFC-)MEC-AGT-2099 | CCI-DAT-1468 | PRO-PID-0037 | Bracket Mount, Vee-notch weirbox level | 3.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
300 | TH00 | 012 | 0LFC | 10 | LIT | CL | 020 |  | 81 | 0120LFC10CL020 | Level Transmitter (Radar) | Wellpad TH12 | Common Steam/Water Dump System | - | Wellpad Pond | Level | N/A | N/A | CL1 | LP Two Phase | atm | atm | -5 | 100 | - | - | mm | 2200 to 6000 | 2350 | 2200 to 6000 | CCI-DET-2706 CCI-DET-2711 | CCI-DAT-1468 | PRO-PID-0037 | Bracket Mount | 7.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
298 | TH00 | 012 | 0LFC | 10 | PIT | CP | 010 |  | 79 | 0120LFC10CP010 | Pressure Indicating Transmitter | Wellpad TH12 | Common Steam/Water Dump System | 0120LFC10-BS010 | Silencer | Pressure | 0120LFC10-BR532-350-CL1 | 350 | CL1 | LP Two Phase | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 0 | 0 to 10 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0037 |  | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
297 | TH00 | 012 | 0LFC | 10 | PI | CP | 510 |  | 78 | 0120LFC10CP510 | Pressure Gauge | Wellpad TH12 | Common Steam/Water Dump System | 0120LFC10-BB010 | Silencer | Pressure | 0120LFC10-BR530-250-CP1 | 250 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 30 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0037 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
292 | TH00 | 012 | 0NDA | 10 | FT | CF | 010 |  | 73 | 0120NDA10CF010 | Flow Transmitter (Orifice Flow) | Wellpad TH12 | Production Piping System | - | Well TH12 | Flow | 0120NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | 0 |  | mbar(g) |  |  | TBC | CCI-DET-2702 | CCI-DAT-1472 Note 2 | PRO-PID-0037 | CEL to SPECIFY Note 3 | 6.3 | Custom Controls | Rosemount | 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A9SC065Q8C0163+ | 4500191995 | 2023-04-19
292.1 | TH00 | 012 | 0NDA | 10 | FT | CF | 020 |  | 73.1 | 0120NDA10CF020 | Flow Transmitter (Orifice Flow) | Wellpad TH12 | Production Piping System | - | Well TH12 | Flow | 0120NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | 0 |  | mbar(g) |  |  | TBC | CCI-DET-2702 | CCI-DAT-1472 Note 2 | PRO-PID-0037 | CEL to SPECIFY Note 3 | 5.6 | Custom Controls | Rosemount | 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4 | 4500193492 | 2023-01-20
296 | TH00 | 012 | 0NDA | 10 | PIT | CP | 010 |  | 77 | 0120NDA10CP010 | Pressure Indicating Transmitter | Wellpad TH12 | Production Piping System | - | Well TH12 | Pressure | N/A | 3 1/8" | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | -1 to 276 | 0 | 0 to 75 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0037 |  | 6.2 | Custom Controls | Rosemount | 2051TG4A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
295 | TH00 | 012 | 0NDA | 10 | PI | CP | 510 |  | 76 | 0120NDA10CP510 | Pressure Gauge | Wellpad TH12 | Production Piping System | - | Well TH12 | Pressure | N/A | 3 1/8" | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 30 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0037 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
294 | TH00 | 012 | 0NDA | 10 | PI | CP | 520 |  | 75 | 0120NDA10CP520 | Pressure Gauge | Wellpad TH12 | Production Piping System | - | Well TH12 FCV Inlet | Pressure | 0120NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 30 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0037 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
293 | TH00 | 012 | 0NDA | 10 | TIT | CT | 010 |  | 74 | 0120NDA10CT010 | Temperature Indicating Transmitter | Wellpad TH12 | Production Piping System | - | Well TH12 | Temperature | 0120NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | °C | 0 to 300 | 235 | 0 to 300 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0037 | Note 7 | 3.7 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-12-01
326 | TH00 | 019 | 0LFC | 10 | LIT | CL | 010 |  | 107 | 0190LFC10CL010 | Level Transmitter (Radar) | Wellpad TH19N | Common Steam/Water Dump System | - | Wellpad Pond | Level | N/A | N/A | CL1 | LP Two Phase | atm | atm | -5 | 100 | - | - | mm | 0 to 6000 | - | 0 to 6000 | CCI-DET-2706 CCI-DET-2711 | CCI-DAT-1468 | PRO-PID-0039 | TH19N No longer | 5.6 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
285 | TH00 | 021 | 0NDA | 10 | FT | CF | 010 |  | 66 | 0210NDA10CF010 | Flow Transmitter (Orifice Flow) | Wellpad TH12 (TH21) | Production Piping System | - | Well TH21 | Flow | 0210NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | 0 |  | mbar(g) |  |  | TBC | CCI-DET-2702 | CCI-DAT-1472 Note 2 | PRO-PID-0037 | CEL to SPECIFY Note 3 | 6.3 | Custom Controls | Rosemount | 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A9SC065Q8C0163+ | 4500191995 | 2023-04-19
285.1 | TH00 | 021 | 0NDA | 10 | FT | CF | 020 |  | 66.1 | 0210NDA10CF020 | Flow Transmitter (Orifice Flow) | Wellpad TH12 (TH21) | Production Piping System | - | Well TH21 | Flow | 0210NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | 0 |  | mbar(g) |  |  | TBC | CCI-DET-2702 | CCI-DAT-1472 Note 2 | PRO-PID-0037 | CEL to SPECIFY Note 3 | 5.6 | Custom Controls | Rosemount | 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4 | 4500193492 | 2023-01-20
290 | TH00 | 021 | 0NDA | 10 | PIT | CP | 010 |  | 71 | 0210NDA10CP010 | Pressure Indicating Transmitter | Wellpad TH12 (TH21) | Production Piping System | - | Well TH21 | Pressure | N/A | 3 1/8" | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | -1 to 276 | 30 | 0 to 75 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0037 |  | 6.2 | Custom Controls | Rosemount | 2051TG4A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
289 | TH00 | 021 | 0NDA | 10 | PI | CP | 510 |  | 70 | 0210NDA10CP510 | Pressure Gauge | Wellpad TH12 (TH21) | Production Piping System | - | Well TH21 | Pressure | N/A | 3 1/8" | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 30 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0037 |  | 3.5 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
287 | TH00 | 021 | 0NDA | 10 | PI | CP | 520 |  | 68 | 0210NDA10CP520 | Pressure Gauge | Wellpad TH12 (TH21) | Production Piping System | - | Well TH21 FCV Inlet | Pressure | 0210NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 30 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0037 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
286 | TH00 | 021 | 0NDA | 10 | TIT | CT | 010 |  | 67 | 0210NDA10CT010 | Temperature Indicating Transmitter | Wellpad TH12 (TH21) | Production Piping System | - | Well TH21 | Temperature | 0210NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | °C | 0 to 300 | 235 | 0 to 300 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0037 | Note 7 | 4.8 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW | 4500191995 | 2023-01-09
283 | TH00 | 026 | 0LFC | 10 | LIT | CL | 010 |  | 64 | 0260LFC10CL010 | Level Transmitter (Radar) | Wellpad TH26 | Common Steam/Water Dump System | 0260LFC10-BB010 | Silencer | Level | N/A | N/A | CL1 | LP Two Phase | atm | atm | -5 | 100 | - | - | mm | 0 to 1300 | 950 | 0 to 1300 | (LFC-)MEC-AGT-2099 | CCI-DAT-1468 | PRO-PID-0036 | Bracket Mount, Vee-notch weirbox level | 3.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
284 | TH00 | 026 | 0LFC | 10 | LIT | CL | 020 |  | 65 | 0260LFC10CL020 | Level Transmitter (Radar) | Wellpad TH26 | Common Steam/Water Dump System | - | Wellpad Pond | Level | N/A | N/A | CL1 | LP Two Phase | atm | atm | -5 | 100 | - | - | mm | 2200 to 6000 | 2350 | 2200 to 6000 | CCI-DET-2706 CCI-DET-2711 | CCI-DAT-1468 | PRO-PID-0036 | Bracket Mount | 7.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
282 | TH00 | 026 | 0LFC | 10 | PIT | CP | 010 |  | 63 | 0260LFC10CP010 | Pressure Indicating Transmitter | Wellpad TH26 | Common Steam/Water Dump System | 0260LFC10-BS010 | Silencer | Pressure | 0260LFC10-BR532-350-CL1 | 350 | CL1 | LP Two Phase | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 0 | 0 to 10 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0036 |  | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
281 | TH00 | 026 | 0LFC | 10 | PI | CP | 510 |  | 62 | 0260LFC10CP510 | Pressure Gauge | Wellpad TH26 | Common Steam/Water Dump System | 0260LFC10-BB010 | Silencer | Pressure | 0260LFC10-BR530-250-CP1 | 250 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 30 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0036 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
276 | TH00 | 026 | 0NDA | 10 | FT | CF | 010 |  | 57 | 0260NDA10CF010 | Flow Transmitter (Orifice Flow) | Wellpad TH26 | Production Piping System | - | Well TH26 | Flow | 0260NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | 0 |  | mbar(g) |  |  | TBC | CCI-DET-2702 | CCI-DAT-1472 Note 2 | PRO-PID-0036 | CEL to SPECIFY Note 3 | 6.3 | Custom Controls | Rosemount | 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A9SC065Q8C0163+ | 4500191995 | 2023-04-19
276.1 | TH00 | 026 | 0NDA | 10 | FT | CF | 020 |  | 57.1 | 0260NDA10CF020 | Flow Transmitter (Orifice Flow) | Wellpad TH26 | Production Piping System | - | Well TH26 | Flow | 0260NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | 0 |  | mbar(g) |  |  | TBC | CCI-DET-2702 | CCI-DAT-1472 Note 2 | PRO-PID-0036 | CEL to SPECIFY Note 3 | 5.6 | Custom Controls | Rosemount | 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4 | 4500193492 | 2023-01-20
280 | TH00 | 026 | 0NDA | 10 | PIT | CP | 010 |  | 61 | 0260NDA10CP010 | Pressure Indicating Transmitter | Wellpad TH26 | Production Piping System | - | Well TH26 | Pressure | N/A | 3 1/8" | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | -1 to 276 | 0 | 0 to 75 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0036 |  | 6.2 | Custom Controls | Rosemount | 2051TG4A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
279 | TH00 | 026 | 0NDA | 10 | PI | CP | 510 |  | 60 | 0260NDA10CP510 | Pressure Gauge | Wellpad TH26 | Production Piping System | - | Well TH26 | Pressure | N/A | 3 1/8" | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 30 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0036 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
278 | TH00 | 026 | 0NDA | 10 | PI | CP | 520 |  | 59 | 0260NDA10CP520 | Pressure Gauge | Wellpad TH26 | Production Piping System | - | Well TH26 FCV Inlet | Pressure | 0260NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 30 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0036 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
277 | TH00 | 026 | 0NDA | 10 | TIT | CT | 010 |  | 58 | 0260NDA10CT010 | Temperature Indicating Transmitter | Wellpad TH26 | Production Piping System | - | Well TH26 | Temperature | 0260NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | °C | 0 to 300 | 235 | 0 to 300 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0036 | Note 7 | 3.7 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-12-01
239 | TH00 | 028 | 0LFC | 10 | LIT | CL | 010 |  | 15 | 0280LFC10CL010 | Level Transmitter (Radar) | Wellpad TH28 | Common Steam/Water Dump System | 0280LFC10-BB010 | Silencer | Level | N/A | N/A | CP1 | Two Phase Production Line | atm | atm | -5 | 100 | - | - | mm | 0 to 1300 | 950 | 0 to 1300 | (LFC-)MEC-AGT-2099 | CCI-DAT-1468 | PRO-PID-0031 | Bracket Mount, Vee-notch weirbox level | 3.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
240 | TH00 | 028 | 0LFC | 10 | LIT | CL | 020 |  | 16 | 0280LFC10CL020 | Level Transmitter (Radar) | Wellpad TH28 | Common Steam/Water Dump System | - | Wellpad Pond | Level | N/A | N/A | CP1 | Two Phase Production Line | atm | atm | -5 | 100 | - | - | mm | 2200 to 6000 | 2350 | 2200 to 6000 | CCI-DET-2706 CCI-DET-2711 | CCI-DAT-1468 | PRO-PID-0031 | Bracket Mount | 7.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
238 | TH00 | 028 | 0LFC | 10 | PIT | CP | 010 |  | 14 | 0280LFC10CP010 | Pressure Indicating Transmitter | Wellpad TH28 | Common Steam/Water Dump System | 0280LFC10-BB010 | Silencer | Pressure | 0280LFC10-BR532-350-CL1 | 350 | CL1 | LP Two Phase | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 0 | 0 to 10 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0031 | No longer Required per Rev J of PID | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
237 | TH00 | 028 | 0LFC | 10 | PI | CP | 510 |  | 13 | 0280LFC10CP510 | Pressure Gauge | Wellpad TH28 | Common Steam/Water Dump System | 0280LFC10-BB010 | Silencer | Pressure | 0280LFC10-BR530-250-CP1 | 250 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 30 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0031 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
232 | TH00 | 028 | 0NDA | 10 | FT | CF | 010 |  | 8 | 0280NDA10CF010 | Flow Transmitter (Orifice Flow) | Wellpad TH28 | Production Piping System | - | Well TH28 | Flow | 0280NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | 0 |  | mbar(g) |  |  | TBC | CCI-DET-2702 | CCI-DAT-1472 Note 2 | PRO-PID-0031 | CEL to SPECIFY Note 3 | 6.3 | Custom Controls | Rosemount | 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A9SC065Q8C0163+ | 4500191995 | 2023-04-19
232.1 | TH00 | 028 | 0NDA | 10 | FT | CF | 020 |  | 8.1 | 0280NDA10CF020 | Flow Transmitter (Orifice Flow) | Wellpad TH28 | Production Piping System | - | Well TH28 | Flow | 0280NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | 0 |  | mbar(g) |  |  | TBC | CCI-DET-2702 | CCI-DAT-1472 Note 2 | PRO-PID-0031 | CEL to SPECIFY Note 3 | 5.6 | Custom Controls | Rosemount | 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4 | 4500193492 | 2023-01-20
236 | TH00 | 028 | 0NDA | 10 | PIT | CP | 010 |  | 12 | 0280NDA10CP010 | Pressure Indicating Transmitter | Wellpad TH28 | Production Piping System | - | Well TH28 | Pressure | N/A | 3 1/8" | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | -1 to 276 | 26.3 | 0 to 75 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0031 |  | 6.2 | Custom Controls | Rosemount | 2051TG4A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
235 | TH00 | 028 | 0NDA | 10 | PI | CP | 510 |  | 11 | 0280NDA10CP510 | Pressure Gauge | Wellpad TH28 | Production Piping System | - | Well TH28 | Pressure | N/A | 3 1/8" | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 26.3 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0031 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
234 | TH00 | 028 | 0NDA | 10 | PI | CP | 520 |  | 10 | 0280NDA10CP520 | Pressure Gauge | Wellpad TH28 | Production Piping System | - | Well TH28 FCV Inlet | Pressure | 0280NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 20.5 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0031 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
233 | TH00 | 028 | 0NDA | 10 | TIT | CT | 010 |  | 9 | 0280NDA10CT010 | Temperature Indicating Transmitter | Wellpad TH28 | Production Piping System | - | Well TH28 | Temperature | 0280NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | °C | 0 to 300 | 216 | 0 to 300 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0031 | Note 7 | 4.8 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW | 4500191995 | 2023-01-09
255 | TH00 | 029 | 0LFC | 10 | LIT | CL | 010 |  | 32 | 0290LFC10CL010 | Level Transmitter (Radar) | Wellpad TH29 | Common Steam/Water Dump System | - | Wellpad Pond | Level | N/A | N/A | CL1 | LP Two Phase | atm | atm | -5 | 100 | - | - | mm | 2200 to 6000 | - | 2200 to 6000 | CCI-DET-2706 CCI-DET-2711 | CCI-DAT-1468 | PRO-PID-0032 | Bracket Mount | 7.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
243 | TH00 | 029 | 0NDB | 10 | FIT | DF | 010 |  | 20 | 0290NDB10CF010 | Flow Transmitter (Orifice Flow) | Wellpad TH29 | Separated Water System | - | Well TH29 | Flow | 0290NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | 0 | 900 | tph | -621 to +621mb |  | 0 to 1450T/H 0 to 612.7mb | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0032 | Notes 3, Note 4, Note 8 | 7.4 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ | 4500191995 | 2023-02-13
246 | TH00 | 029 | 0NDB | 10 | PIT | DP | 010 |  | 23 | 0290NDB10CP010 | Pressure Indicating Transmitter | Wellpad TH29 | Separated Water System | - | Well TH29 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 15 | 0 to 50 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0032 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
245 | TH00 | 029 | 0NDB | 10 | PI | CP | 510 |  | 22 | 0290NDB10CP510 | Pressure Gauge | Wellpad TH29 | Separated Water System | - | Well TH29 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0032 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
244 | TH00 | 029 | 0NDB | 10 | PI | CP | 520 |  | 21 | 0290NDB10CP520 | Pressure Gauge | Wellpad TH29 | Separated Water System | - | Well TH29 FCV Inlet | Pressure | 0290NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0032 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
269 | TH00 | 030 | 0NDA | 10 | FT | CF | 010 |  | 50 | 0300NDA10CF010 | Flow Transmitter (Orifice Flow) | Wellpad TH26 (TH30) | Production Piping System | - | Well TH30 | Flow | 0300NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | 0 |  | mbar(g) |  |  | TBC | CCI-DET-2702 | CCI-DAT-1472 Note 2 | PRO-PID-0036 | CEL to SPECIFY Note 3 | 6.3 | Custom Controls | Rosemount | 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A9SC065Q8C0163+ | 4500191995 | 2023-04-19
269.1 | TH00 | 030 | 0NDA | 10 | FT | CF | 020 |  | 50.1 | 0300NDA10CF020 | Flow Transmitter (Orifice Flow) | Wellpad TH26 (TH30) | Production Piping System | - | Well TH30 | Flow | 0300NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | 0 |  | mbar(g) |  |  | TBC | CCI-DET-2702 | CCI-DAT-1472 Note 2 | PRO-PID-0036 | CEL to SPECIFY Note 3 | 5.6 | Custom Controls | Rosemount | 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4 | 4500193492 | 2023-01-20
274 | TH00 | 030 | 0NDA | 10 | PIT | CP | 010 |  | 55 | 0300NDA10CP010 | Pressure Indicating Transmitter | Wellpad TH26 (TH30) | Production Piping System | - | Well TH30 | Pressure | N/A | 3 1/8" | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | -1 to 276 | 30 | 0 to 75 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0036 |  | 6.2 | Custom Controls | Rosemount | 2051TG4A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
273 | TH00 | 030 | 0NDA | 10 | PI | CP | 510 |  | 54 | 0300NDA10CP510 | Pressure Gauge | Wellpad TH26 (TH30) | Production Piping System | - | Well TH30 | Pressure | N/A | 3 1/8" | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 30 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0036 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
271 | TH00 | 030 | 0NDA | 10 | PI | CP | 520 |  | 52 | 0300NDA10CP520 | Pressure Gauge | Wellpad TH26 (TH30) | Production Piping System | - | Well TH30 FCV Inlet | Pressure | 0300NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 30 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0036 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
270 | TH00 | 030 | 0NDA | 10 | TIT | CT | 010 |  | 51 | 0300NDA10CT010 | Temperature Indicating Transmitter | Wellpad TH26 (TH30) | Production Piping System | - | Well TH30 | Temperature | 0300NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | °C | 0 to 300 | 235 | 0 to 300 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0036 | Note 7 | 3.7 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-12-01
247 | TH00 | 031 | 0NDB | 10 | FIT | DF | 010 |  | 24 | 0310NDB10CF010 | Flow Transmitter (Orifice Flow) | Wellpad TH29 (TH31) | Separated Water System | - | Well TH31 | Flow | 0310NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | 0 | 1400 | tph | -621 to +621mb |  | 0 to 1450T/H 0 to 612.7mb | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0032 | Notes 3, Note 4, Note 8 | 7.4 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ | 4500191995 | 2023-02-13
250 | TH00 | 031 | 0NDB | 10 | PIT | DP | 010 |  | 27 | 0310NDB10CP010 | Pressure Indicating Transmitter | Wellpad TH29 (TH31) | Separated Water System | - | Well TH31 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 15 | 0 to 50 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0032 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
249 | TH00 | 031 | 0NDB | 10 | PI | CP | 501 |  | 26 | 0310NDB10CP501 | Pressure Gauge | Wellpad TH29 (TH31) | Separated Water System | - | Well TH31 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0032 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
248 | TH00 | 031 | 0NDB | 10 | PI | CP | 520 |  | 25 | 0310NDB10CP520 | Pressure Gauge | Wellpad TH29 (TH31) | Separated Water System | - | Well TH31 FCV Inlet | Pressure | 0310NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0032 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
225 | TH00 | 034 | 0NDA | 10 | FT | CF | 010 |  | 1 | 0360NDA10CF010 | Flow Transmitter (Orifice Flow) | Wellpad TH28 (TH36) | Production Piping System | - | Well TH36 | Flow | 0340NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | 0 |  | mbar(g) |  |  | TBC | CCI-DET-2702 | CCI-DAT-1472 Note 2 | PRO-PID-0031 | CEL to SPECIFY Note 3 New KKS Tag, old: 0340NDA10CF010 | 6.4 | Custom Controls | Rosemount | 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A9SC065Q8C0163+ | 4500191995 | 2023-04-19
225.1 | TH00 | 034 | 0NDA | 10 | FT | CF | 020 |  | 1.1 | 0360NDA10CF020 | Flow Transmitter (Orifice Flow) | Wellpad TH28 (TH36) | Production Piping System | - | Well TH36 | Flow | 0340NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | 0 |  | mbar(g) |  |  | TBC | CCI-DET-2702 | CCI-DAT-1472 Note 2 | PRO-PID-0031 | CEL to SPECIFY Note 3 New KKS Tag, old: 0340NDA10CF020 | 6.4 | Custom Controls | Rosemount | 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4 | 4500193492 | 2023-01-20
231 | TH00 | 034 | 0NDA | 10 | PIT | CP | 010 |  | 7 | 0360NDA10CP010 | Pressure Indicating Transmitter | Wellpad TH28 (TH36) | Production Piping System | - | Well TH36 | Pressure | N/A | 3 1/8" | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | -1 to 276 | 26.3 | 0 to 75 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0031 | New KKS Tag, old: 0340NDA10CP010 | 6.4 | Custom Controls | Rosemount | 2051TG4A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
230 | TH00 | 034 | 0NDA | 10 | PI | CP | 510 |  | 6 | 0360NDA10CP510 | Pressure Gauge | Wellpad TH28 (TH36) | Production Piping System | - | Well TH36 | Pressure | N/A | 3 1/8" | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 26.3 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0031 |  | 6.4 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
227 | TH00 | 034 | 0NDA | 10 | PI | CP | 520 |  | 3 | 0360NDA10CP520 | Pressure Gauge | Wellpad TH28 (TH36) | Production Piping System | - | Well TH36 FCV Inlet | Pressure | 0340NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | bar(g) | 0 to 100 | 20.5 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0031 |  | 6.4 | Wika | Wika | 72039884+14503369+0763349 | 4500189704 | 2022-11-10
226 | TH00 | 034 | 0NDA | 10 | TIT | CT | 010 |  | 2 | 0360NDA10CT010 | Temperature Indicating Transmitter | Wellpad TH28 (TH36) | Production Piping System | - | Well TH36 | Temperature | 0340NDA10-BR010-400-CP1 | 400 | CP1 | Two Phase Production Line | Full Vac | 74 | -5 | 273 | - | - | °C | 0 to 300 | 216 | 0 to 300 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0031 | Note 7 New KKS Tag, old: 0340NDA10CT010 | 6.4 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-12-01
251 | TH00 | EA3 | 0NDB | 10 | FIT | CF | 010 |  | 28 | 0350NDB10CF010 | Flow Transmitter (Orifice Flow) | Wellpad TH29 (TH35) | Separated Water System | - | Well TH35 | Flow | EA30NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | 0 | 1400 | tph | -621 to +621mb |  | 0 to 1450T/H 0 to 612.7mb | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0032 | CEL to CONFIRM RANGE Notes 3, Note 4, Note 8 | 7.4 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ | 4500191995 | 2023-02-13
254 | TH00 | EA3 | 0NDB | 10 | PIT | DP | 010 |  | 31 | 0350NDB10CP010 | Pressure Indicating Transmitter | Wellpad TH29 (TH35) | Separated Water System | - | Well TH35 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 30 | 0 to 50 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0032 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
253 | TH00 | EA3 | 0NDB | 10 | PI | CP | 510 |  | 30 | 0350NDB10CP510 | Pressure Gauge | Wellpad TH29 (TH35) | Separated Water System | - | Well TH35 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 30 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0032 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
252 | TH00 | EA3 | 0NDB | 10 | PI | CP | 520 |  | 29 | 0350NDB10CP520 | Pressure Gauge | Wellpad TH29 (TH35) | Separated Water System | - | Well TH35 FCV Inlet | Pressure | 0350NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0032 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
307 | TH00 | 037 | 0NDB | 10 | FIT | CF | 010 |  | 88 | 0370NDB10CF010 | Flow Transmitter (Orifice Flow) | Wellpad TH37 | Separated Water System | - | Well TH37 | Flow | 0370NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | 0 | 1000 | tph | -621 to +621mb |  | 0 to 1450T/H 0 to 612.7mb | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0038 | Notes 3, Note 4, Note 8. | 7.4 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ | 4500191995 | 2023-02-13
310 | TH00 | 37 | 0NDB | 10 | PIT | CP | 010 |  | 91 | 0370NDB10CP010 | Pressure Indicating Transmitter | Wellpad TH37 | Separated Water System | - | Well TH37 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 15 | 0 to 50 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0038 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
305 | TH00 | 037 | 0NDB | 10 | PI | CP | 510 |  | 86 | 0370NDB10CP510 | Pressure Gauge | Wellpad TH37 | Separated Water System | - | Well TH37 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0038 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
304 | TH00 | 37 | 0NDB | 10 | PI | CP | 520 |  | 85 | 0370NDB10CP520 | Pressure Gauge | Wellpad TH37 | Separated Water System | - | Well TH37 FCV Inlet | Pressure | 0370NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0038 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
303 | TH00 | 038 | 0NDB | 10 | FIT | CF | 010 |  | 84 | 0380NAI74+K4:AP+K74:AP74 | Flow Transmitter (Orifice Flow) | Wellpad TH37 (TH38) | Separated Water System | - | Well TH38 | Flow | 0380NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | 0 | 1000 | tph |  |  | 0 to 1000 | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0038 | SPARE Notes 3, Note 4, Note 8. | 5.6 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P120A3SB065Q8+ | 4500191995 | 2023-02-13
306 | TH00 | 038 | 0NDB | 10 | PIT | CP | 010 |  | 87 | 0380NDB10CP010 | Pressure Indicating Transmitter | Wellpad TH37 (TH38) | Separated Water System | - | Well TH38 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 15 | 0 to 50 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0038 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
309 | TH00 | 038 | 0NDB | 10 | PI | CP | 501 |  | 90 | 0380NDB10CP501 | Pressure Gauge | Wellpad TH37 (TH38) | Separated Water System | - | Well TH38 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0038 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
308 | TH00 | 38 | 0NDB | 10 | PI | CP | 520 |  | 89 | 0380NDB10CP520 | Pressure Gauge | Wellpad TH37 (TH38) | Separated Water System | - | Well TH38 FCV Inlet | Pressure | 0380NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0038 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
316 | TH00 | 191 | 0NDB | 10 | PI | CP | 510 |  | 97 | 1910NDB10CP510 | Pressure Gauge | Wellpad TH19N (TH19N_1) | Separated Water System | - | Well TH19N-1 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0039 | HOLD 1 | 2.8 | Wika | Wika | 72039876+14503369+0731277 (Spare) | 4500189704 | Spare
315 | TH00 | 191 | 0NDB | 10 | PI | CP | 520 |  | 96 | 1910NDB10CP520 | Pressure Gauge | Wellpad TH19N (TH19N_1) | Separated Water System | - | Well TH19N-1 FCV Inlet | Pressure | 1910NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0039 | HOLD 1 | 2.8 | Wika | Wika | 72039876+14503369+0731277 (Spare) | 4500189704 | Spare
320 | TH00 | 192 | 0NDB | 10 | PI | CP | 501 |  | 101 | 1920NDB10CP501 | Pressure Gauge | Wellpad TH19N (TH19N_2) | Separated Water System | - | Well TH19N-2 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0039 | HOLD 1 | 2.8 | Wika | Wika | 72039876+14503369+0731277 (Spare) | 4500189704 | Spare
319 | TH00 | 192 | 0NDB | 10 | PI | CP | 520 |  | 100 | 1920NDB10CP520 | Pressure Gauge | Wellpad TH19N (TH19N_2) | Separated Water System | - | Well TH19N-2 FCV Inlet | Pressure | 1920NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0039 | HOLD 1 | 2.8 | Wika | Wika | 72039876+14503369+0731277 (Spare) | 4500189704 | Spare
324 | TH00 | 193 | 0NDB | 10 | PI | CP | 510 |  | 105 | 1930NDB10CP510 | Pressure Gauge | Wellpad TH19N (TH19N_3) | Separated Water System | - | Well TH19N-3 | Pressure | N/A | 3 1/8" | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0039 | HOLD 1 | 2.8 | Wika | Wika | 72039876+14503369+0731277 (Spare) | 4500189704 | Spare
323 | TH00 | 193 | 0NDB | 10 | PI | CP | 520 |  | 104 | 1930NDB10CP520 | Pressure Gauge | Wellpad TH19N (TH19N_3) | Separated Water System | - | Well TH19N-3 FCV Inlet | Pressure | 1930NDB10-BR010-300-CR1 | 300 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0039 | HOLD 1 | 2.8 | Wika | Wika | 72039876+14503369+0731277 (Spare) | 4500189704 | Spare
16 | TH00 | L05 | 0NDA | 10 | PIT | CP | 010 |  | 16 | L050NDA10CP010 | Pressure Indicating Transmitter | TH12 Two Phase Pipeline | Production Piping System | L050NDA10-AA030 | TH12 Two Phase Isolation Valve | Pressure | L050NDA10-BR030-750-CH1 | 750 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | bar(g) | -1 to 55 | 21.27 | 0 to 35 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0011 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
288 | TH00 | L05 | 0NDA | 10 | PI | CP | 532 |  | 69 | L050NDA10CP532 | Pressure Gauge | TH12 Two Phase Pipeline | Production Piping System | - | Wellpad TH12 | Pressure | L050NDA10-BR30-750-CH1 | 750 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | bar(g) | 0 to 40 | 25 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0037 |  | 3.2 | Wika | Wika | 72039883+14503369+0763349 | 4500189704 | 2022-11-10
17 | TH00 | L05 | 0NDA | 10 | TIT | CT | 010 |  | 17 | L050NDA10CT010 | Temperature Indicating Transmitter | TH12 Two Phase Pipeline | Production Piping System | L050NDA10-AA030 | TH12 Two Phase Isolation Valve Inlet | Temperature | L050NDA10-BR030-750-CH1 | 750 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 217.9 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1465 | PRO-PID-0011 | Note 7 | 4.8 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0350SLAR1C2B1UAE065TBXW+114CM0275TAC2SC075AQ5Q8R21XW | 4500191995 | 2023-01-09
291 | TH00 | L05 | 0NDA | 10 | TIT | CT | 030 |  | 72 | L050NDA10CT030 | Temperature Indicating Transmitter | TH12 Two Phase Pipeline | Production Piping System | - | Wellpad TH12 | Temperature | L050NDA10-BR30-750-CH1 | 750 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 215 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0037 | Note 7 | 4.8 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0350SLAR1C2B1UAE065TBXW+114CM0275TAC2SC075AQ5Q8R21XW | 4500191995 | 2023-01-09
10 | TH00 | L06 | 0NDA | 10 | PIT | CP | 010 |  | 10 | L060NDA10CP010 | Pressure Indicating Transmitter | TH28 Two Phase Pipeline | Production Piping System | L060NDA10-AA030 | TH28 Two Phase Isolation Valve | Pressure | L060NDA10-BR030-800-CH1 | 800 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | bar(g) | -1 to 55 | 21.27 | 0 to 35 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0011 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
229 | TH00 | L06 | 0NDA | 10 | PIT | CP | 531 |  | 5 | L060NDA10CP531 | Pressure Indicating Transmitter | TH28 Two Phase Pipeline | Production Piping System | - | Wellpad TH28 | Pressure | L060NDA10-BR030-750-CH1 | 750 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | bar(g) | -1 to 55 | 20.5 | 0 to 50 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0031 | SPARE replaced by L060NDA10CP532 New KKS Tag, old: L060NDA10CP531 | 5.6 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11+ | 4500191995 | 2023-01-13
229.1 | TH00 | L06 | 0NDA | 10 | PI | CP | 532 |  | 5.1 | L060NDA10CP532 | Pressure Gauge | TH28 Two Phase Pipeline | Production Piping System | - | Wellpad TH28 | Pressure | 750 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | 243 | - | - | bar(g) | -1 to 55 | 20.5 | 0 to 50 | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0031 |  | 3.2 | Wika | Wika | 72039884+14503369+0763349 | 4500195012 | 2022-11-10
11 | TH00 | L06 | 0NDA | 10 | TIT | CT | 010 |  | 11 | L060NDA10CT010 | Temperature Indicating Transmitter | TH28 Two Phase Pipeline | Production Piping System | L060NDA10-AA030 | TH28 Two Phase Isolation Valve Inlet | Temperature | L060NDA10-BR030-800-CH1 | 800 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 217.9 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1465 | PRO-PID-0011 | Note 7 | 4.8 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0370SLAR1C2B1UAE065TBXW+114CM0295TAC2SC075AQ5Q8R21XW | 4500191995 | 2023-01-09
3 | TH00 | L06 | 0NDA | 10 | TIT | CT | 030 |  | 4 | L060NDA10CT030 | Temperature Indicating Transmitter | TH28 Two Phase Pipeline | Production Piping System | - | Wellpad TH28 | Temperature | L060NDA10-BR030-750-CH1 | 750 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 216 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0031 | Note 7 | 4.8 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0350SLAR1C2B1UAE065TBXW+114CM0275TAC2SC075AQ5Q8R21XW | 4500191995 | 2023-01-09
264 | TH00 | L06 | 0NDA | 10 | TI | CT | 510 |  | 43 | L060NDA10CT510 | Temperature Indicator (Gauge) | TH28 Two Phase Pipeline | Production Piping System | - | Two Phase Cross Country Line | Temperature | L060NDA10-BR030-750-CH1 | 750 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 215 | - | CCI-DET-2703 | CCI-DAT-1463 | PRO-PID-0034 | Note 7 | 3.2 | Wika | Wika | 72039934+72039931 | 4500189704 | 2022-11-10
265 | TH00 | L06 | 0NDA | 10 | TI | CT | 511 |  | 46 | L060NDA10CT511 | Temperature Indicator (Gauge) | TH28 Two Phase Pipeline | Production Piping System | L070LFC10-BB020 | Silencer | Temperature | L060NDA10-BR450-200-CH1 | 200 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 215 | - | CCI-DET-2703 | CCI-DAT-1463 | PRO-PID-0034 | Note 7 | 3.2 | Wika | Wika | 72039935+72039932 | 4500189704 | 2022-11-10
[9 empty] | 44 | L060NDA10CT520 | Temperature Indicator (Gauge) | TH28 Two Phase Pipeline | Production Piping System | - | Two Phase Cross Country Line | Temperature | L060NDA10-BR030-800-CH1 | 800 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 215 | - | CCI-DET-2703 | CCI-DAT-1463 | PRO-PID-0034 | Note 7 | 3.2 | Wika | Wika | 72039934+72039931 | 4500189704 | 2022-11-10
[9 empty] | 45 | L060NDA10CT521 | Temperature Indicator (Gauge) | TH28 Two Phase Pipeline | Production Piping System | - | Two Phase Cross Country Line | Temperature | L060NDA10-BR460-100-CH1 | 100 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 215 | - | CCI-DET-2703 | CCI-DAT-1463 | PRO-PID-0034 | Note 7 | 3.2 | Wika | Wika | 72040072+72040071 | 4500189704 | 2022-11-10
266 | TH00 | L07 | 0LFC | 10 | LT | CL | 010 |  | 47 | L070LFC10CL010 | Level Transmitter (Radar) | TH26 Two Phase Pipeline | Common Steam/Water Dump System | - | Wellpad Pond | Level | N/A | N/A | N/A | Two Phase | atm | atm | -5 | 100 | - | - | mm | 2200 to 6000 | - | 2200 to 6000 | CCI-DET-2706 CCI-DET-2711 | CCI-DAT-1468 | PRO-PID-0034 | Bracket Mount | 7.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
4 | TH00 | L07 | 0NDA | 10 | PIT | CP | 010 |  | 4 | L070NDA10CP010 | Pressure Indicating Transmitter | TH26 Two Phase Pipeline | Production Piping System | L070NDA10-AA030 | TH26 Two Phase Isolation Valve | Pressure | L070NDA10-BR030-800-CH1 | 800 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | bar(g) | -1 to 55 | 21.27 | 0 to 35 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0011 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
272 | TH00 | L07 | 0NDA | 10 | PI | CP | 532 |  | 53 | L070NDA10CP532 | Pressure Gauge | TH26 Two Phase Pipeline | Production Piping System | - | Wellpad TH26 | Pressure | L070NDA10-BR030-750-CH1 | 750 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | bar(g) | 0 to 40 | 25 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0036 |  | 3.2 | Wika | Wika | 72039883+14503369+0763349 | 4500189704 | 2022-11-10
5 | TH00 | L07 | 0NDA | 10 | TIT | CT | 010 |  | 5 | L070NDA10CT010 | Temperature Indicating Transmitter | TH26 Two Phase Pipeline | Production Piping System | L070NDA10-AA030 | TH26 Two Phase Isolation Valve Inlet | Temperature | L070NDA10-BR030-800-CH1 | 800 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 217.9 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1465 | PRO-PID-0011 | Note 7 | 4.8 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0370SLAR1C2B1UAE065TBXW+114CM0295TAC2SC075AQ5Q8R21XW | 4500191995 | 2023-01-09
275 | TH00 | L07 | 0NDA | 10 | TIT | CT | 030 |  | 56 | L070NDA10CT030 | Temperature Indicating Transmitter | TH26 Two Phase Pipeline | Production Piping System | - | Wellpad TH26 | Temperature | L070NDA10-BR30-750-CH1 | 750 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 215 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0036 | Note 7 | 4.8 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0350SLAR1C2B1UAE065TBXW+114CM0275TAC2SC075AQ5Q8R21XW | 4500191995 | 2023-01-09
239 | TH00 | L07 | 0NDA | 10 | TI | CT | 510 |  | 39 | L070NDA10-CT510 | Temperature Indicator (Gauge) | TH26 Two Phase Pipeline | Production Piping System | - | Two Phase Cross Country Line | Temperature | L070NDA10-BR030-750-CH1 | 750 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 215 | - | CCI-DET-2703 | CCI-DAT-1463 | PRO-PID-0034 | Note 7 | 3.2 | Wika | Wika | 72039934+72039931 | 4500189704 | 2022-11-10
262 | TH00 | L07 | 0NDA | 10 | TI | CT | 511 |  | 40 | L070NDA10CT511 | Temperature Indicator (Gauge) | TH26 Two Phase Pipeline | Production Piping System | - | Two Phase Cross Country Line | Temperature | L070NDA10-BR030-750-CH1 | 750 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 215 | - | CCI-DET-2703 | CCI-DAT-1463 | PRO-PID-0034 | Note 7 | 3.2 | Wika | Wika | 72039934+72039931 | 4500189704 | 2022-11-10
263 | TH00 | L07 | 0NDA | 10 | TI | CT | 512 |  | 42 | L070NDA10CT512 | Temperature Indicator (Gauge) | TH26 Two Phase Pipeline | Production Piping System | L070LFC10-BB020 | Silencer | Temperature | L070NDA10-BR440-200-CH1 | 200 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 215 | - | CCI-DET-2703 | CCI-DAT-1463 | PRO-PID-0034 | Note 7 | 3.2 | Wika | Wika | 72039935+72039932 | 4500189704 | 2022-11-10
262 | TH00 | L07 | 0NDA | 10 | TI | CT | 511 |  | 41 | L070NDA10CT522 | Temperature Indicator (Gauge) | TH26 Two Phase Pipeline | Production Piping System | - | Two Phase Cross Country Line | Temperature | L070NDA10-BR450-100-CH1 | 100 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 215 | - | CCI-DET-2703 | CCI-DAT-1463 | PRO-PID-0034 | Note 7 | 3.2 | Wika | Wika | 72040072+72040071 | 4500189704 | 2022-11-10
256 | TH00 | L15 | 0NAB | 10 | PI | CP | 510 |  | 33 | L150NAB10CP510 | Pressure Gauge | Condensate Pipeline To TH11 | Condensate System | - | Wellpad TH11 | Pressure | L150NAB10-BR010-630-S11 | 630 | S11 | GF & Condensate | Full Vac | 13.5 | -5 | 50 | - | - | bar(g) | 0 to 16 | 5 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0033 |  | 3.2 | Wika | Wika | 72039879+14503369+0731277 | 4500189704 | 2022-11-10
267 | TH00 | L19 | 0NDB | 10 | PIT | CP | 010 |  | 48 | L190NDB10CP010 | Pressure Indicating Transmitter | SGW Pipeline To TH29 Well Pad | Separated Water System | - | SGW Cross Country Line | Pressure | L190NDB10-BR001-500-CR1 | 500 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 30 | -1 to 50 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0035 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
[9 empty] | 18 | L190NDB10CP011 | Pressure Indicating Transmitter | SWG Pipeline to TH29 Wellpad | Separated Water System |  | Wellpad TH29 | Pressure | L190NDB10-BR002-500-CR1 | 500 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 15 | 0 to 50 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0032 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
242 | TH00 | L19 | 0NDB | 10 | PI | CP | 510 |  | 19 | L190NDB10CP510 | Pressure Gauge | SWG Pipeline to TH29 Wellpad | Separated Water System | - | Wellpad TH29 | Pressure | L190NDB10-BR002-500-CR1 | 500 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0032 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
241 | TH00 | L19 | 0NDB | 10 | TIT | CT | 010 |  | 17 | L190NDB10CT010 | Temperature Indicating Transmitter | SWG Pipeline to TH29 Wellpad | Separated Water System | - | Wellpad TH29 | Temperature | L190NDB10-BR002-500-CR1 | 500 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | °C | 0 to 250 | 123 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0032 | Note 7 | 5.6 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-12-01
268 | TH00 | L20 | 0NDB | 10 | PIT | CP | 010 |  | 49 | L200NDB10CP010 | Pressure Indicating Transmitter | SGW Pipeline To TH29 Well Pad | Separated Water System | - | SGW Cross Country Line | Pressure | L200NDB10-BR001-500-CR1 | 500 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 30 | -1 to 50 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0035 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
[10 empty] | L210NDB10CP011 | Pressure Indicating Transmitter | SWG Pipeline to TH29 Wellpad | Separated Water System |  | Wellpad TH29 | Pressure | L190NDB10-BR002-500-CR1 | 500 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 15 | 0 to 50 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0032 | SPARE replaced by L210NDA10CP510 New KKS Tag, old: L210NDB10CP011 | 5.6 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
302 | TH00 | L21 | 0NDB | 10 | PI | CP | 510 |  | 83 | L210NDB10CP510 | Pressure Gauge | SGW Pipeline To Wellpad TH37 | Separated Water System | - | Wellpad TH37 | Pressure | L210NDB10-BR001-500-CR1 | 500 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0038 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
301 | TH00 | L21 | 0NDB | 10 | TIT | CT | 010 |  | 82 | L210NDB10CT010 | Temperature Indicating Transmitter | SGW Pipeline To Wellpad TH37 | Separated Water System | - | Wellpad TH37 | Temperature | L210NDB10-BR001-500-CR1 | 500 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | °C | 0 to 250 | 123 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0038 |  | 5.6 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-12-01
313 | TH00 | L22 | 0NDB | 10 | PI | CP | 510 |  | 94 | L220NDB10CP510 | Pressure Gauge | Wellpad TH19N (TH19N_1) | Separated Water System | - | Wellpad TH19N | Pressure | L220NDB10-BR001-500-CR1 | 500 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | 0 to 60 | 15 | - | Vendor Supplied | CCI-DAT-1460 | PRO-PID-0039 | HOLD 1 | 2.8 | Wika | Wika | 72039876+14503369+0731277 (Spare) | 4500189704 | Spare
311 | TH00 | LCP | 0LFC | 10 | LIT | CL | 010 |  | 92 | 0370LFC10CL010 | Level Transmitter (Radar) | Wellpad TH37 | Common Steam/Water Dump System | - | Wellpad TH37 Pond | Level | N/A | N/A | CL1 | LP Two Phase | atm | atm | -5 | 100 | - | - | mm | 2200 to 6000 | - | 2200 to 6000 | CCI-DET-2706 CCI-DET-2711 | CCI-DAT-1468 | PRO-PID-0038 | Bracket Mount, New KKS Tag, old: LCP0LFC10CL010 | 7.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
342 | TH00 | P02 | 0GAC | 20 | LT | CL | 010 |  | 99 | P020GWA20CL010 | Level Transmitter (Radar) | Pump Station | Seal Water System | P020GAC20-BB001 | Seal Water Tank 1 | Level | N/A | 50 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | mm | Note 9 | N/A | Note 9 | CCI-DET-2706 PRO-DAT-0078 | CCI-DAT-1468 | PRO-PID-0041 | 2"/DN50 CL300. Verify bridle nozzle dimension with vessel manufacturer. New KKS Tag, old: P020GAC20CL010 | 5.6 | Custom Controls | Rosemount | 5408F1SHA2NA1R2ABCAA2M5DA1Q4Q8+751AM1NAB+ | 4500191995 | 2022-11-10
343 | TH00 | P02 | 0GAC | 20 | LG | CL | 011 |  | 100 | P020GAC20CL011 | Level Gauge | Pump Station | Seal Water System | P020GAC20-BB001 | Seal Water Tank 1 | Level | N/A | 50 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | mm | Note 9 | N/A | Refer to Notes | CCI-DET-2705 PRO-DAT-0078 | CCI-DAT-1471 | PRO-PID-0041 | 2"/DN50 CL300. Verify bridle nozzle dimension with vessel manufacturer. |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
344 | TH00 | P02 | 0GAC | 20 | LT | CL | 020 |  | 101 | P020GWA20CL020 | Level Transmitter (Radar) | Pump Station | Seal Water System | P020GAC20-BB002 | Seal Water Tank 2 | Level | N/A | 50 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | mm | Note 9 | N/A | 0 to 8 | CCI-DET-2706 PRO-DAT-0078 | CCI-DAT-1468 | PRO-PID-0041 | 2"/DN50 CL300. Verify bridle nozzle dimension with vessel manufacturer. New KKS Tag, old: P020GAC20CL020 | 5.6 | Custom Controls | Rosemount | 5408F1SHA2NA1R2ABCAA2M5DA1Q4Q8+751AM1NAB+ | 4500191995 | 2022-11-10
345 | TH00 | P02 | 0GAC | 20 | LG | CL | 021 |  | 102 | P020GAC20CL021 | Level Gauge | Pump Station | Seal Water System | P020GAC20-BB002 | Seal Water Tank 2 | Level | N/A | 50 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | mm | Note 9 | N/A | Refer to Notes | CCI-DET-2705 PRO-DAT-0078 | CCI-DAT-1471 | PRO-PID-0041 | 2"/DN50 CL300. Verify bridle nozzle dimension with vessel manufacturer. |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
402 | TH00 | S02 | 0GKA | 21 | PIT | CP | 520 |  | 178 | S020GKA21CP520 | Pressure Indicating Transmitter | Separation Plant | Potable Water System | - | Potable Water Pump Outlet Pressure | Pressure | P020GKA21-BR043-50-S8 | 50 | S8 | Potable Water | Full Vac | 10 | -5 | 75 | - | - | bar(g) | -1 to 55 | 3.49 | 0 to 10 | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0040 | Was P020GAC20CP020. Repurposed as S020GKA21CP520 | 6.2 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
340 | TH00 | P02 | 0GAC | 20 | PI | CP | 010 |  | 97 | P020GAC20CP510 | Pressure Gauge | Pump Station | Seal Water System | P020GAC20-AT010 | Deoxygenated Process Water Filter Inlet | Pressure | P020GAC20-BR074-25-S9 | 25 | S9 | Process Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0041 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
341 | TH00 | P02 | 0GAC | 20 | PI | CP | 011 |  | 98 | P020GAC20CP511 | Pressure Gauge | Pump Station | Seal Water System | P020GAC20-AT010 | Deoxygenated Process Water Filter Outlet | Pressure | P020GAC20-BR075-25-S9 | 25 | S9 | Process Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0041 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
337 | TH00 | P02 | 0GAC | 30 | PI | CP | 090 |  | 94 | P020GAC30CP590 | Pressure Gauge | Pump Station | Seal Water System | P020GAC30-AH010 | Seal Water Return Fin Fan Cooler | Pressure | P020GAC30-BR070-50-S9 | 50 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0041 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
338 | TH00 | P02 | 0GAC | 30 | PI | CP | 091 |  | 95 | P020GAC30CP591 | Pressure Gauge | Pump Station | Seal Water System | P020GAC30-AH010 | Seal Water Return Fin Fan Cooler | Pressure | P020GAC30-BR072-50-S9 | 50 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0041 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
339 | TH00 | P02 | 0GAC | 30 | TE | CT | 050 |  | 96 | P020GWA30CT050 | Temperature Element | Pump Station | Seal Water System | P020GAC30-AH010 | Seal Water Return Fin Fan Cooler | Temperature | P020GAC30-BR072-50-S9 | 50 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | °C | 0 to 250 | 32 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0041 | Note 7 New KKS Tag, old: P020GAC30CT050 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW | 4500191995 | 2022-11-10
376 | TH00 | P02 | 0PCB | 20 | LIT | DL | 010 |  | 133 | P020PCB20CL010 | Level Transmitter (DP) | Pump Station | VSD Cooling Water System | S020PCB20-BB010 | Coolant Expansion Vessel | Level | N/A | N/A | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | mm | TBC | 773 | TBC | CCI-DET-2704 | CCI-DAT-1467 | PRO-PID-0044 | New KKS Tag, old: P020GWA20CL010 | 5.6 | Custom Controls | Rosemount | 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | 4500191995 | 2022-11-10
347 | TH00 | P02 | 0GAC | 21 | PDIT | DP | 001 |  | 104 | P020GWA21CP001 | Pressure Differential Transmitter | Pump Station | Seal Water System |  | Seal Water In Line Filter Differential | Pressure | P020GAC21-BR005-50-S9 | 50 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | mbar(g) | -2500 to 2500 | 0 | 0 to 250mbar | CCI-DET-2702 | CCI-DAT-1462 | PRO-PID-0042 |  | 4 | Custom Controls | Rosemount | 2051CD3A02A1BS5M4Q4 c/w 0305RC52B11B4++ | 4500191995 | 2022-11-10
346 | TH00 | P02 | 0GAC | 21 | PIT | CP | 002 |  | 103 | P020GWA21CP002 | Pressure Indicating Transmitter | Pump Station | Seal Water System |  | Seal Water | Pressure | P020GAC21-BR005-50-S9 | 50 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | -1 to 2.1 | -0.34 | -0.7 to +0.7 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0042 |  | 6.2 | Custom Controls | Rosemount | 2051TG1A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
348 | TH00 | P02 | 0GAC | 21 | PIT | DP | 010 |  | 105 | P020GWA22CP010 | Pressure Indicating Transmitter | Pump Station | Seal Water System | P020GAC21-AP010 | Seal Water Pump Skid Outlet | Pressure | P020GAC21-BR023-50-S9 | 50 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | -1 to 55 | 11.77 | 0 to 15 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0042 |  | 6.2 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
351 | TH00 | P02 | 0GAC | 21 | PI | CP | 510 |  | 108 | P020GWA22CP510 | Pressure Gauge | Pump Station | Seal Water System |  | Seal Water Pumps Outlet | Pressure | P020GAC21-BR026-50-S9 | 50 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0042 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
349 | TH00 | P02 | 0GAC | 21 | PIT | DP | 020 |  | 106 | P020GWA23CP020 | Pressure Indicating Transmitter | Pump Station | Seal Water System | P020GAC21-AP020 | Seal Water Pump B Outlet | Pressure | P020GAC21-BR024-25-S9 | 25 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | -1 to 55 | 11.77 | 0 to 15 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0042 | SPARE as now a pump skid New KKS Tag, old: P020GWA23CP020 | 5.6 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
366 | TH00 | P02 | 0GAC | 21 | PIT | DP | 030 |  | 107 | P020GWA24CP030 | Pressure Indicating Transmitter | Pump Station | Seal Water System | P020GAC21-AP030 | Seal Water Pump C Outlet | Pressure | P020GAC21-BR025-25-S9 | 25 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | -1 to 55 | 11.77 | 0 to 15 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0042 | SPARE as now a pump skid New KKS Tag, old: P020GWA24CP030 | 5.6 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
353 | TH00 | P02 | 0GAC | 30 | FIT | DF | 010 |  | 110 | P020GWA30CF010 | Flow Transmitter (Magnetic) | Pump Station | Seal Water System | S020GAC30-CF012 | SGW Reinjection Pump A Seal Water Inlet | Flow | S020GAC30-BR031-20-S9 | 20 (See Notes) | S9 | Seal Water | Full Vac | 15 | -5 | 75 | 0 | 0.17 | l/m | 0 to 10 | 8 | 0 to 10 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0043 | Was P020GWA30CF010 | 5 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | 4500191995 | 2022-11-10
357 | TH00 | P02 | 0GAC | 30 | FIT | DF | 011 |  | 114 | P020GWA30CF011 | Flow Transmitter (Magnetic) | Pump Station | Seal Water System | S020GAC30-CF012 | SGW Reinjection Pump A Seal Water Inlet | Flow | S020GAC30-BR032-20-S9 | 20 (See Notes) | S9 | Seal Water | Full Vac | 15 | -5 | 75 | 0 | 0.17 | l/m | 0 to 10 | 8 | 0 to 10 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0043 | Was P020GWA30CF011 | 5 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | 4500191995 | 2022-11-10
359 | TH00 | P02 | 0GAC | 30 | FIT | DF | 020 |  | 116 | P020GWA31CF020 | Flow Transmitter (Magnetic) | Pump Station | Seal Water System | S020GAC30-CF022 | SGW Reinjection Pump B Seal Water Inlet | Flow | S020GAC30-BR041-20-S9 | 20 (See Notes) | S9 | Seal Water | Full Vac | 15 | -5 | 75 | 0 | 0.17 | l/m | 0 to 10 | 8 | 0 to 10 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0043 | Was P020GWA30CF020 | 5 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | 4500191995 | 2022-11-10
363 | TH00 | P02 | 0GAC | 30 | FIT | DF | 021 |  | 120 | P020GWA31CF021 | Flow Transmitter (Magnetic) | Pump Station | Seal Water System | S020GAC30-CF022 | SGW Reinjection Pump B Seal Water Intlet | Flow | S020GAC30-BR042-20-S9 | 20 (See Notes) | S9 | Seal Water | Full Vac | 15 | -5 | 75 | 0 | 0.17 | l/m | 0 to 10 | 8 | 0 to 10 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0043 | Was P020GWA30CF021 | 5 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | 4500191995 | 2022-11-10
365 | TH00 | P02 | 0GAC | 30 | FIT | DF | 030 |  | 122 | P020GWA32CF030 | Flow Transmitter (Magnetic) | Pump Station | Seal Water System | S020GAC30-CF032 | SGW Reinjection Pump C Seal Water Intlet | Flow | S020GAC30-BR051-20-S9 | 20 (See Notes) | S9 | Seal Water | Full Vac | 15 | -5 | 75 | 0 | 0.17 | l/m | 0 to 10 | 8 | 0 to 10 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0043 | Was P020GWA30CF030 | 5 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | 4500191995 | 2022-11-10
369 | TH00 | P02 | 0GAC | 30 | FIT | DF | 031 |  | 126 | P020GWA32CF031 | Flow Transmitter (Magnetic) | Pump Station | Seal Water System | S020GAC30-CF032 | SGW Reinjection Pump C Seal Water Intlet | Flow | S020GAC30-BR052-20-S9 | 20 (See Notes) | S9 | Seal Water | Full Vac | 15 | -5 | 75 | 0 | 0.17 | l/m | 0 to 10 | 8 | 0 to 10 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0043 | Was P020GWA30CF031 | 5 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | 4500191995 | 2022-11-10
371 | TH00 | P02 | 0GAC | 30 | FIT | DF | 040 |  | 128 | P020GWA33CF040 | Flow Transmitter (Magnetic) | Pump Station | Seal Water System | S020GAC30-CF042 | Cond Pump A Seal Water Inlet A Flow | Flow | S020GAC30-BR061-20-S9 | 20 (See Notes) | S9 | Seal Water | Full Vac | 15 | -5 | 75 | 0 | 0.17 | l/m | 0 to 10 | 8 | 0 to 10 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0043 | Was P020GWA30CF040 | 5 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | 4500191995 | 2022-11-10
375 | TH00 | P02 | 0GAC | 30 | FIT | DF | 041 |  | 132 | P020GWA33CF041 | Flow Transmitter (Magnetic) | Pump Station | Seal Water System | S020GAC30-CF042 | Cond Pump A Seal Water Inlet A Flow | Flow | S020GAC30-BR062-20-S9 | 20 (See Notes) | S9 | Seal Water | Full Vac | 15 | -5 | 75 | 0 | 0.17 | l/m | 0 to 10 | 8 | 0 to 10 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0043 | SPARE | 7.6 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | 4500191995 | 2022-11-10
352 | TH00 | P02 | 0GAC | 30 | PI | CP | 501 |  | 109 | P020GWA30CP501 | Pressure Gauge | Pump Station | Seal Water System | S020GAC30-CF012 | Cond Pump A Seal Water Inlet B Flow | Pressure | S020GAC30-BR033-20-S9 | 20 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0043 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
356 | TH00 | P02 | 0GAC | 30 | PI | CP | 502 |  | 113 | P020GWA30CP502 | Pressure Gauge | Pump Station | Seal Water System | S020GAC30-CF012 | SGW Reinjection Pump A Seal Water Outlet | Pressure | S020GAC30-BR034-20-S9 | 20 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0043 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
355 | TH00 | P02 | 0GAC | 30 | PI | CP | 503 |  | 112 | P020GWA30CP503 | Pressure Gauge | Pump Station | Seal Water System | S020GAC30-CF012 | SGW Reinjection Pump A Seal Water Outlet | Pressure | S020GAC30-BR035-25-S9 | 25 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0043 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
354 | TH00 | P02 | 0GAC | 30 | TT | CT | 010 |  | 111 | P020GWA30CT010 | Temperature Transmitter | Pump Station | Seal Water System | S020GAC30-CF012 | SGW Reinjection Pump A Seal Water Outlet | Temperature | S020GAC30-BR035-25-S9 | 25 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | °C | 0 to 250 | 32 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0043 | Note 7 | 5.6 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW | 4500191995 | 2022-12-01
360 | TH00 | P02 | 0GAC | 30 | TT | CT | 020 |  | 117 | P020GWA31CT020 | Temperature Transmitter | Pump Station | Seal Water System | S020GAC30-CF022 | SGW Reinjection Pump B Seal Water Outlet | Temperature | S020GAC30-BR045-25-S9 | 25 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | °C | 0 to 250 | 32 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0043 | Note 7 New KKS Tag, old: P020GWA30CT020 | 5.6 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW | 4500191995 | 2022-12-01
382 | TH00 | P02 | 0GAC | 30 | TT | CT | 030 |  | 123 | P020GWA32CT030 | Temperature Transmitter | Pump Station | Seal Water System | S020GAC30-CF032 | SGW Reinjection Pump C Seal Water Outlet | Temperature | S020GAC30-BR055-25-S9 | 25 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | °C | 0 to 250 | 32 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0043 | Note 7 New KKS Tag, old: P020GWA30CT030 | 5.6 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW | 4500191995 | 2022-12-01
372 | TH00 | P02 | 0GAC | 30 | TT | CT | 040 |  | 129 | P020GWA33CT040 | Temperature Transmitter | Pump Station | Seal Water System | S020GAC30-CF042 | SGW Reinjection Pump D Seal Water Outlet | Temperature | S020GAC30-BR065-25-S9 | 25 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | °C | 0 to 250 | 32 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0043 | Note 7 New KKS Tag, old: P020GWA30CT040 | 5.6 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW | 4500191995 | 2023-01-09
358 | TH00 | P02 | 0GAC | 30 | PI | CP | 511 |  | 115 | P020GWA31CP511 | Pressure Gauge | Pump Station | Seal Water System | S020GAC30-CF022 | SGW Reinjection Pump B Seal Water Outlet | Pressure | S020GAC30-BR043-20-S9 | 20 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0043 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
362 | TH00 | P02 | 0GAC | 30 | PI | CP | 512 |  | 119 | P020GWA31CP512 | Pressure Gauge | Pump Station | Seal Water System | S020GAC30-CF022 | SGW Reinjection Pump B Seal Water Outlet | Pressure | S020GAC30-BR044-20-S9 | 20 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0043 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
361 | TH00 | P02 | 0GAC | 30 | PI | CP | 513 |  | 118 | P020GWA31CP513 | Pressure Gauge | Pump Station | Seal Water System | S020GAC30-CF022 | SGW Reinjection Pump B Seal Water Outlet | Pressure | S020GAC30-BR045-25-S9 | 25 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0043 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
364 | TH00 | P02 | 0GAC | 30 | PI | CP | 521 |  | 121 | P020GWA32CP521 | Pressure Gauge | Pump Station | Seal Water System | S020GAC30-CF032 | SGW Reinjection Pump C Seal Water Outlet | Pressure | S020GAC30-BR053-20-S9 | 20 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0043 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
368 | TH00 | P02 | 0GAC | 30 | PI | CP | 522 |  | 125 | P020GWA32CP522 | Pressure Gauge | Pump Station | Seal Water System | S020GAC30-CF032 | SGW Reinjection Pump C Seal Water Outlet | Pressure | S020GAC30-BR054-20-S9 | 20 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0043 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
367 | TH00 | P02 | 0GAC | 30 | PI | CP | 523 |  | 124 | P020GWA32CP523 | Pressure Gauge | Pump Station | Seal Water System | S020GAC30-CF032 | SGW Reinjection Pump C Seal Water Outlet | Pressure | S020GAC30-BR055-25-S9 | 25 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0043 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
370 | TH00 | P02 | 0GAC | 30 | PI | CP | 531 |  | 127 | P020GWA33CP531 | Pressure Gauge | Pump Station | Seal Water System | S020GAC30-CF042 | SGW Reinjection Pump D Seal Water Outlet | Pressure | S020GAC30-BR063-20-S9 | 20 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0043 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
374 | TH00 | P02 | 0GAC | 30 | PI | CP | 532 |  | 131 | P020GWA33CP532 | Pressure Gauge | Pump Station | Seal Water System | S020GAC30-CF042 | SGW Reinjection Pump D Seal Water Outlet | Pressure | S020GAC30-BR064-20-S9 | 20 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0043 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
373 | TH00 | P02 | 0GAC | 30 | PI | CP | 533 |  | 130 | P020GWA33CP533 | Pressure Gauge | Pump Station | Seal Water System | S020GAC30-CF042 | SGW Reinjection Pump D Seal Water Outlet | Pressure | S020GAC30-BR065-25-S9 | 25 | S9 | Seal Water | Full Vac | 15 | -5 | 75 | - | - | bar(g) | 0 to 15 | 11.77 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0043 |  | 3.5 | Wika | Wika | 72039876+14503369+ | 4500189704 | 2022-08-05
| TH00 | P02 | 0GWB | 10 | LT | CL | 010 |  |  | P020GWB10CL010 | Level Transmitter (Radar) | Pump Station | Seal Water System |  | GFHP Seal Water Tank | Level | N/A | N/A | N/A | Raw Water | Full Vac | 10 | -5 | 75 | - | - | mm | 0 to 3000 | N/A | 0 to 3000 | CCI-DET-2706 PRO-DAT-0078 | CCI-DAT-1468 | PRO-PID-0056 | Flange mount DN50 | 4.9 | Instrumatics | Vega | PS21.XXXXXGMHB+GFL-PULS.GG | 4500196238 | 2023-01-12
| TH00 | P02 | 0GWB | 10 | LI | CL | 011 |  |  | P020GWB10CL011 | Level Indicator (Remote) | Pump Station | Seal Water System |  | GFHP Seal Water Tank | Level | N/A | N/A | N/A | Raw Water | Full Vac | 10 | -5 | 75 | - | - | mm | 0 to 3000 | N/A | 0 to 3000 |  |  | PRO-PID-0056 |  | 4.9 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | P02 | 0GWB | 10 | LT | CP | 510 |  |  | P020GWB10CP510 | Pressure Differential Transmitter | Pump Station | Seal Water System |  | GFHP Seal Water System | Pressure |  | 50 |  | Raw Water | Full Vac | 10 | -5 | 75 |  |  | bar(g) | 0 to 2.5 | 1.7 | 0 to 2.5 | CCI-DET-2702 | CCI-DAT-1460 | PRO-PID-0056 | New KKS Tag, old: P020GWB10CP510 | 5.9 | Custom Controls | Rosemount | 2051CD3A02A1BS5M4Q4+0305RC52B11B4 | 4500197800 | 2023-03-20
| TH00 | P02 | 0GWB | 21 | LT | CF | 010 |  |  | P020GWB21CF010 | Flow Transmitter (Magnetic) | Pump Station | Seal Water System |  | GFHP Seal Water System | Flow |  | 10 |  | Raw Water | Full Vac | 16 | -5 | 75 | 0 | 8 | l/m | 0 to 10 | N/A | 0 to 10 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0056 | New KKS Tag, old: P020GWB21CF010 | 5.6 | IFM | IFM | SM6020, SMR12GGX50KG/US-100 | 4500196549 | 2022-11-21
| TH00 | P02 | 0GWB | 21 | LT | CF | 020 |  |  | P020GWB21CF020 | Flow Transmitter (Magnetic) | Pump Station | Seal Water System |  | GFHP Seal Water System | Flow |  | 10 |  | Raw Water | Full Vac | 16 | -5 | 75 | 0 | 30 | l/m | 0 to 35 | N/A | 0 to 35 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0056 | New KKS Tag, old: P020GWB21CF020 | 5.6 | IFM | IFM | SM6020, SMR12GGX50KG/US-100 | 4500196549 | 2022-11-21
| TH00 | P02 | 0GWB | 21 | LT | CP | 511 |  |  | P020GWB21CP511 | Pressure Gauge | Pump Station | Seal Water System |  | GFHP Seal Water System | Pressure |  | 15 |  | Raw Water | Full Vac | 16 | -5 | 75 |  |  | bar(g) | 0 to 25 | 13 | 0 to 25 |  | CCI-DAT-1460 | PRO-PID-0056 |  | 5.8 | Wika | Wika | 72039878+14298395 | 4500197977 | 2023-03-09
| TH00 | P02 | 0GWB | 21 | LT | CP | 521 |  |  | P020GWB21CP521 | Pressure Gauge | Pump Station | Seal Water System |  | GFHP Seal Water System | Pressure |  | 15 |  | Raw Water | Full Vac | 16 | -5 | 75 |  |  | bar(g) | 0 to 25 | 13 | 0 to 25 |  | CCI-DAT-1460 | PRO-PID-0056 |  | 5.8 | Wika | Wika | 72039878+14298395 | 4500197977 | 2023-03-09
| TH00 | P02 | 0GWB | 22 | LT | CF | 010 |  |  | P020GWB22CF010 | Flow Transmitter (Magnetic) | Pump Station | Seal Water System |  | GFHP Seal Water System | Flow |  | 10 |  | Raw Water | Full Vac | 16 | -5 | 75 | 0 | 8 | l/m | 0 to 10 | N/A | 0 to 10 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0056 | New KKS Tag, old: P020GWB22CF010 | 5.6 | IFM | IFM | SM6020, SMR12GGX50KG/US-100 | 4500196549 | 2022-11-21
| TH00 | P02 | 0GWB | 22 | LT | CF | 020 |  |  | P020GWB22CF020 | Flow Transmitter (Magnetic) | Pump Station | Seal Water System |  | GFHP Seal Water System | Flow |  | 10 |  | Raw Water | Full Vac | 16 | -5 | 75 | 0 | 30 | l/m | 0 to 35 | N/A | 0 to 35 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0056 | New KKS Tag, old: P020GWB22CF020 | 5.6 | IFM | IFM | SM6020, SMR12GGX50KG/US-100 | 4500196549 | 2022-11-21
| TH00 | P02 | 0GWB | 22 | LT | CP | 511 |  |  | P020GWB22CP511 | Pressure Gauge | Pump Station | Seal Water System |  | GFHP Seal Water System | Pressure |  | 50 |  | Raw Water | Full Vac | 16 | -5 | 75 |  |  | bar(g) | 0 to 25 | 13 | 0 to 25 |  | CCI-DAT-1460 | PRO-PID-0056 |  | 5.8 | Wika | Wika | 72039878+14298395 | 4500197977 | 2023-03-09
| TH00 | P02 | 0GWB | 22 | LT | CP | 521 |  |  | P020GWB22CP521 | Pressure Gauge | Pump Station | Seal Water System |  | GFHP Seal Water System | Pressure |  | 15 |  | Raw Water | Full Vac | 16 | -5 | 75 |  |  | bar(g) | 0 to 25 | 13 | 0 to 25 |  | CCI-DAT-1460 | PRO-PID-0056 |  | 5.8 | Wika | Wika | 72039878+14298395 | 4500197977 | 2023-03-09
186 | TH00 | P02 | 0LFC | 20 | FIT | DF | 010 |  | 79 | P020LFC20CF010 | Flow Transmitter (Orifice Flow) | Pump Station | Common Steam/Water Dump System |  | GFHP Pump Station Outlet | Flow | P020LFC20-BR003-500-S11 | 500 | S11 | GF & Condensate | Full Vac | 13.5 | -5 | 50 | 0 | 1550 | tph | 0 to 1200 | 850 | 0 to 1550 | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0028 | Note 3, Note 8 | 5.6 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P200A3SC065Q8+ | 4500191995 | 2023-02-13
182 | TH00 | P02 | 0LFC | 20 | LIT | DL | 001 |  | 71 | P020LFC20CL001 | Level Transmitter (Radar) | Pump Station | Common Steam/Water Dump System |  | Geothermal Fluid Holding Pond | Level | N/A | 100 | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm | 0 to 10000 | N/A | 0 to 10000 | CCI-DET-2706 STR-DET-0147 | CCI-DAT-1468 | PRO-PID-0028 | Pipe Stub Mount DN100 CL150 | 3.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
183 | TH00 | P02 | 0LFC | 20 | LIT | DL | 002 |  | 72 | P020LFC20CL002 | Level Transmitter (Radar) | Pump Station | Common Steam/Water Dump System |  | Geothermal Fluid Holding Pond | Level | N/A | 100 | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm | 0 to 10000 | N/A | 0 to 10000 | CCI-DET-2706 STR-DET-0147 | CCI-DAT-1468 | PRO-PID-0028 | Pipe Stub Mount DN100 CL150 | 3.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
184 | TH00 | P02 | 0LFC | 20 | LIT | DL | 003 |  | 73 | P020LFC20CL003 | Level Transmitter (Radar) | Pump Station | Common Steam/Water Dump System |  | Geothermal Fluid Holding Pond | Level | N/A | 100 | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm | 0 to 10000 | N/A | 0 to 10000 | CCI-DET-2706 STR-DET-0147 | CCI-DAT-1468 | PRO-PID-0028 | Pipe Stub Mount DN100 CL150 | 3.2 | Instrumatics | Vega | PSC21.XXXXXGBHB+DIS82.IXHKIMACX | 4500189544 | 2022-11-10
| TH00 | P02 | 0LFC | 10 | LIT |  |  |  | 74 | P020LFC20CL010 | Level Transmitter (Hydrostatic) | Pump Station | Common Steam/Water Dump System |  | Geothermal Fluid Holding Pond | Level | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm | 0 to 6000 | 0 | 0 to 6000 | GCV-DET-0179 | CCI-DAT-1480 | PRO-PID-0028 |  | 3.2 | Instrumatics | Vega | B86.IXCMAXAGDHXATMKM | 4500189928 | 2022-11-10
| TH00 | P02 | 0LFC | 20 | LIT |  |  |  | 77 | P020LFC20CL020 | Level Transmitter (Hydrostatic) | Pump Station | Common Steam/Water Dump System |  | Geothermal Fluid Holding Pond | Level | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm | 0 to 6000 | 0 | 0 to 6000 | GCV-DET-0179 | CCI-DAT-1480 | PRO-PID-0028 |  | 3.2 | Instrumatics | Vega | B86.IXCMAXAGDHXATMKM | 4500189928 | 2022-11-10
| TH00 | P02 | 0LFC | 30 | LIT |  |  |  | 75 | P020LFC20CL030 | Level Transmitter (Hydrostatic) | Pump Station | Common Steam/Water Dump System |  | Geothermal Fluid Holding Pond | Level | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm | 0 to 6000 | 0 | 0 to 6000 | GCV-DET-0179 | CCI-DAT-1480 | PRO-PID-0028 |  | 3.2 | Instrumatics | Vega | B86.IXCMAXAGDHXATMKM | 4500189928 | 2022-11-10
| TH00 | P02 | 0LFC | 40 | LIT |  |  |  | 76 | P020LFC20CL040 | Level Transmitter (Hydrostatic) | Pump Station | Common Steam/Water Dump System |  | Geothermal Fluid Holding Pond | Level | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm | 0 to 6000 | 0 | 0 to 6000 | GCV-DET-0179 | CCI-DAT-1480 | PRO-PID-0028 |  | 3.2 | Instrumatics | Vega | B86.IXCMAXAGDHXATMKM | 4500189928 | 2022-11-10
181 | TH00 | P02 | 0LFC | 20 | PIT | CP | 010 |  | 70 | P020LFC20CP010 | Pressure Indicating Transmitter | Pump Station | Common Steam/Water Dump System | P020LFC20-AA191 | GFHP Pump Station Outlet | Pressure | P020LFC20-BR191-100-S11 | 100 | S11 | GF & Condensate | Full Vac | 13.5 | -5 | 50 | - | - | bar(g) | -1 to 55 | 16 | 0 to 25 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0028 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
185 | TH00 | P02 | 0LFC | 20 | TT | DT | 011 |  | 78 | P020LFC20CT011 | Temperature Transmitter | Pump Station | Common Steam/Water Dump System |  | Geothermal Fluid Holding Pond | Temperature | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | °C | 0 to 250 | 45 | 0 to 250 | STR-DET-0147 | CCI-DAT-1465 | PRO-PID-0028 | Submersible RTD with 15m cable | 6.3 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+Wika Submersible Sensor+ | 45001918881 | 2023-03-21
171 | TH00 | P02 | 0LFC | 20 | TE | CT | 012 |  | 60 | P020LFC20CT012 | Temperature Element | Pump Station | Common Steam/Water Dump System | P020LFC20-AP010 | GFHP Pump A | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
172 | TH00 | P02 | 0LFC | 20 | TE | CT | 013 |  | 61 | P020LFC20CT013 | Temperature Element | Pump Station | Common Steam/Water Dump System | P020LFC20-AP010 | GFHP Pump A | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
173 | TH00 | P02 | 0LFC | 20 | TE | CT | 014 |  | 62 | P020LFC20CT014 | Temperature Element | Pump Station | Common Steam/Water Dump System | P020LFC20-AP010 | GFHP Pump A | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
174 | TH00 | P02 | 0LFC | 20 | TE | CT | 015 |  | 63 | P020LFC20CT015 | Temperature Element | Pump Station | Common Steam/Water Dump System | P020LFC20-AP010 | GFHP Pump A | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
175 | TH00 | P02 | 0LFC | 20 | TE | CT | 016 |  | 64 | P020LFC20CT016 | Temperature Element | Pump Station | Common Steam/Water Dump System | P020LFC20-AP010 | GFHP Pump A | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
176 | TH00 | P02 | 0LFC | 20 | TE | CT | 022 |  | 65 | P020LFC20CT022 | Temperature Element | Pump Station | Common Steam/Water Dump System | P020LFC20-AP020 | GFHP Pump B | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
177 | TH00 | P02 | 0LFC | 20 | TE | CT | 023 |  | 66 | P020LFC20CT023 | Temperature Element | Pump Station | Common Steam/Water Dump System | P020LFC20-AP020 | GFHP Pump B | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
178 | TH00 | P02 | 0LFC | 20 | TE | CT | 024 |  | 67 | P020LFC20CT024 | Temperature Element | Pump Station | Common Steam/Water Dump System | P020LFC20-AP020 | GFHP Pump B | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
179 | TH00 | P02 | 0LFC | 20 | TE | CT | 025 |  | 68 | P020LFC20CT025 | Temperature Element | Pump Station | Common Steam/Water Dump System | P020LFC20-AP020 | GFHP Pump B | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
180 | TH00 | P02 | 0LFC | 20 | TE | CT | 026 |  | 69 | P020LFC20CT026 | Temperature Element | Pump Station | Common Steam/Water Dump System | P020LFC20-AP020 | GFHP Pump B | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
165 | TH00 | P02 | 0LFC | 20 | VXT | CY | 010 |  | 54 | P020LFC20CY010 | Vibration Transmitter | Pump Station | Common Steam/Water Dump System | P020LFC20-AP010 | GFHP Pump A | Vibration | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
166 | TH00 | P02 | 0LFC | 20 | VYT | CY | 011 |  | 55 | P020LFC20CY011 | Vibration Transmitter | Pump Station | Common Steam/Water Dump System | P020LFC20-AP010 | GFHP Pump A | Vibration | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
167 | TH00 | P02 | 0LFC | 20 | ST | CY | 012 |  | 56 | P020LFC20CY012 | Speed Indicator | Pump Station | Common Steam/Water Dump System | P020LFC20-AP010 | GFHP Pump A | Speed/Frequecny | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
168 | TH00 | P02 | 0LFC | 20 | VXT | CY | 020 |  | 57 | P020LFC20CY020 | Vibration Transmitter | Pump Station | Common Steam/Water Dump System | P020LFC20-AP020 | GFHP Pump B | Vibration | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
169 | TH00 | P02 | 0LFC | 20 | VYT | CY | 021 |  | 58 | P020LFC20CY021 | Vibration Transmitter | Pump Station | Common Steam/Water Dump System | P020LFC20-AP020 | GFHP Pump B | Vibration | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
170 | TH00 | P02 | 0LFC | 20 | ST | CY | 022 |  | 59 | P020LFC20CY022 | Speed Indicator | Pump Station | Common Steam/Water Dump System | P020LFC20-AP020 | GFHP Pump B | Speed/Frequecny | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0022 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
187 | TH00 | P02 | 0NAB | 10 | FIT | DF | 010 |  | 80 | P020NAB10CF010 | Flow Transmitter (Magnetic) | Pump Station | Condensate System |  | Condensate Pump Station Inlet | Flow | P020NAB10-BR001-300-S11 | 300 | S11 | GF & Condensate | Full Vac | 13.5 | -5 | 50 | 0 | 10000 | tph | 0 to 10,000 | 7600 | 0 to 600 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0028 | 12" DN300/CL150 | 5.6 | Custom Controls | Rosemount | 8750WDMT2A2FNSA120CA1M4Q4Q8+Included in Flowtube Model+ | 4500191995 | 2022-11-10
188 | TH00 | P02 | 0NAB | 10 | PDIT | CP | 010 |  | 81 | P020NAB10CP010 | Pressure Differential Transmitter | Pump Station | Condensate System | P020NAB10-AT010 | Inlet Filter | Pressure | P020NAB10-BR001-300-S11 | 300 | S11 | GF & Condensate | Full Vac | 13.5 | -5 | 50 | - | - | mbar(g) | -2500 to 2500 | 0 | 0 to 250mbar | CCI-DET-2702 | CCI-DAT-1462 | PRO-PID-0028 |  | 3.2 | Custom Controls | Rosemount | 2051CD3A02A1BS5M4Q4 c/w 0305RC52B11B4++ | 4500191995 | 2022-11-10
189 | TH00 | P02 | 0NAB | 10 | PIT | DP | 011 |  | 82 | P020NAB10CP011 | Pressure Indicating Transmitter | Pump Station | Condensate System | P020NAB10-AP010 | Condensate Pump A Inlet | Pressure | P020NAB10-BR001-300-S11 | 300 | S11 | GF & Condensate | Full Vac | 13.5 | -5 | 50 | - | - | bar(g) | -0.97 to 137.89 | 0.8 | 0 to 15 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0028 |  | 7.8 | Custom Controls | Rosemount | 3051S2CG5A2E12A1BB4D2M5Q4Q8+0306RT22BA11 | 4500200505 | 2023-06-09
198 | TH00 | P02 | 0NAB | 10 | PIT | DP | 012 |  | 91 | P020NAB10CP012 | Pressure Indicating Transmitter | Pump Station | Condensate System | P020NAB10-AP010 | Condensate Pump A Outlet | Pressure | P020NAB10-BR004-300-S11 | 300 | S11 | GF & Condensate | Full Vac | 13.5 | -5 | 50 | - | - | bar(g) | -0.97 to 137.89 | 3.5 | 0 to 15 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0028 |  | 7.8 | Custom Controls | Rosemount | 3051S2CG5A2E12A1BB4D2M5Q4Q8+0306RT22BA11 | 4500200505 | 2023-06-09
200 | TH00 | P02 | 0NAB | 10 | PIT | CP | 030 |  | 93 | P020NAB10CP030 | Pressure Indicating Transmitter | Pump Station | Condensate System |  | Condensate Reinjection | Pressure | P020NAB10-BR004-500-S11 | 500 | S11 | GF & Condensate | Full Vac | 13.5 | -5 | 50 | - | - | bar(g) | -0.97 to 137.89 | 3.5 | 0 to 15 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0028 |  | 7.8 | Custom Controls | Rosemount | 3051S2CG5A2E12A1BB4D2M5Q4Q8+0306RT22BA11 | 4500200505 | 2023-06-09
193 | TH00 | P02 | 0NAB | 10 | TE | CT | 012 |  | 86 | P020NAB10CT012 | Temperature Element | Pump Station | Condensate System | P020NAB10-AP010 | Condensate Pump | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0021 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
194 | TH00 | P02 | 0NAB | 10 | TE | CT | 013 |  | 87 | P020NAB10CT013 | Temperature Element | Pump Station | Condensate System | P020NAB10-AP010 | Condensate Pump | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0021 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
195 | TH00 | P02 | 0NAB | 10 | TE | CT | 014 |  | 88 | P020NAB10CT014 | Temperature Element | Pump Station | Condensate System | P020NAB10-AP010 | Condensate Pump | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0021 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
196 | TH00 | P02 | 0NAB | 10 | TE | CT | 015 |  | 89 | P020NAB10CT015 | Temperature Element | Pump Station | Condensate System | P020NAB10-AP010 | Condensate Pump | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0021 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
197 | TH00 | P02 | 0NAB | 10 | TE | CT | 016 |  | 90 | P020NAB10CT016 | Temperature Element | Pump Station | Condensate System | P020NAB10-AP010 | Condensate Pump | Temperature | N/A | N/A | S11 | GF & Condensate | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0021 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
199 | TH00 | P02 | 0NAB | 10 | TE | CT | 030 |  | 92 | P020NAB10CT030 | Temperature Element | Pump Station | Condensate System |  | Condensate Reinjection | Temperature | P020NAB10-BR004-500-S11 | 500 | S11 | GF & Condensate | Full Vac | 13.5 | -5 | 50 | - | - | °C | 0 to 250 | 45 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0028 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
190 | TH00 | P02 | 0NAB | 10 | VXT | CY | 010 |  | 83 | P020NAB10CY010 | Vibration Transmitter | Pump Station | Condensate System | P020NAB10-AP010 | Condensate Pump | Vibration | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0021 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
191 | TH00 | P02 | 0NAB | 10 | VYT | CY | 011 |  | 84 | P020NAB10CY011 | Vibration Transmitter | Pump Station | Condensate System | P020NAB10-AP010 | Condensate Pump | Vibration | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0021 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
192 | TH00 | P02 | 0NAB | 10 | ST | CY | 012 |  | 85 | P020NAB10CY012 | Speed Indicator | Pump Station | Condensate System | P020NAB10-AP010 | Condensate Pump | Speed/Frequecny | N/A | N/A | S11 | GF & Condensate | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0021 | PRO-PID-0028 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
129 | TH00 | P02 | 0NDB | 10 | FIT | CF | 010 |  | 18 | P020NDB10CF010 | Flow Transmitter (Orifice Flow) | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A Outlet | Flow | P020NDB10-BR031-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | 0 | 1264 | tph | -621 to +621mb |  | 0 to 1262 tph 0 to 620.8 mb | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0026 | Note 3, Note 8 | 7.4 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A6SC065Q8+ | 4500191995 | 2023-02-13
146 | TH00 | P02 | 0NDB | 10 | FIT | CF | 020 |  | 35 | P020NDB10CF020 | Flow Transmitter (Orifice Flow) | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B Outlet | Flow | P020NDB10-BR032-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | 0 | 1264 | tph | -621 to +621mb |  | 0 to 1262 tph 0 to 620.8 mb | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0026 | Note 3, Note 8 | 7.4 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A6SC065Q8+ | 4500191995 | 2023-02-13
163 | TH00 | P02 | 0NDB | 10 | FIT | CF | 030 |  | 52 | P020NDB10CF030 | Flow Transmitter (Orifice Flow) | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C Outlet | Flow | P020NDB10-BR033-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | 0 | 1264 | tph | -621 to +621mb |  | 0 to 1262 tph 0 to 620.8 mb | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0026 | Note 3, Note 8 | 7.4 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P160A6SC065Q8+ | 4500191995 | 2023-02-13
114 | TH00 | P02 | 0NDB | 10 | PIT | CP | 011 |  | 3 | P020NDB10CP011 | Pressure Indicating Transmitter | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A Inlet | Pressure | P020NDB10-BR021-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 35 | 0 to 45 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0026 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
128 | TH00 | P02 | 0NDB | 10 | PIT | CP | 014 |  | 17 | P020NDB10CP014 | Pressure Indicating Transmitter | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A Outlet | Pressure | P020NDB10-BR031-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 35 | 0 to 45 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0026 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
115 | TH00 | P02 | 0NDB | 10 | PDI | CP | 015 |  | 4 | P020NDB10CP015 | Pressure Differential Indicator | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A Inlet | Pressure | P020NDB10-BR021-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | mbar(g) | 0 to 500 | 0 | - | CCI-DET-2702 | CCI-DAT-1462 | PRO-PID-0026 |  | 3.2 | Wika | Wika | 72039917++11585791 | 4500189704 | 2022-11-10
132 | TH00 | P02 | 0NDB | 10 | PIT | CP | 021 |  | 21 | P020NDB10CP021 | Pressure Indicating Transmitter | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B Inlet | Pressure | P020NDB10-BR022-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 35 | 0 to 45 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0026 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
145 | TH00 | P02 | 0NDB | 10 | PIT | CP | 024 |  | 34 | P020NDB10CP024 | Pressure Indicating Transmitter | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B Outlet | Pressure | P020NDB10-BR032-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 35 | 0 to 45 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0026 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
130 | TH00 | P02 | 0NDB | 10 | PDI | CP | 025 |  | 19 | P020NDB10CP025 | Pressure Differential Indicator | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B Inlet | Pressure | P020NDB10-BR022-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | mbar(g) | 0 to 500 | 0 | . | CCI-DET-2702 | CCI-DAT-1462 | PRO-PID-0026 |  | 3.2 | Wika | Wika | 72039917++11585791 | 4500189704 | 2022-11-10
149 | TH00 | P02 | 0NDB | 10 | PIT | CP | 031 |  | 38 | P020NDB10CP031 | Pressure Indicating Transmitter | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C Inlet | Pressure | P020NDB10-BR023-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 35 | 0 to 45 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0026 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
162 | TH00 | P02 | 0NDB | 10 | PIT | CP | 034 |  | 51 | P020NDB10CP034 | Pressure Indicating Transmitter | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C Outlet | Pressure | P020NDB10-BR033-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 35 | 0 to 45 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0026 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
147 | TH00 | P02 | 0NDB | 10 | PDI | CP | 035 |  | 36 | P020NDB10CP035 | Pressure Differential Indicator | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C Inlet | Pressure | P020NDB10-BR023-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | mbar(g) | 0 to 500 | 0 | - | CCI-DET-2702 | CCI-DAT-1462 | PRO-PID-0026 |  | 3.2 | Wika | Wika | 72039917++11585791 | 4500189704 | 2022-11-10
164 | TH00 | P02 | 0NDB | 10 | PIT | CP | 040 |  | 53 | P020NDB10CP040 | Pressure Indicating Transmitter | Pump Station | Separated Water System |  | SGW Reinjection Pump Station Outlet | Pressure | P020NDB10-BR050-750-CR1 | 750 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | -1 to 55 | 35 | 0 to 45 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0026 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
116 | TH00 | P02 | 0NDB | 10 | PI | CP | 512 |  | 5 | P020NDB10CP512 | Pressure Gauge | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A Inlet | Pressure | N/A | N/A | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | See Notes | 35 | - | Vendor Supplied | PRO-DAT-0020 CCI-DAT-1460 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
127 | TH00 | P02 | 0NDB | 10 | PI | CP | 513 |  | 16 | P020NDB10CP513 | Pressure Gauge | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A Outlet | Pressure | N/A | N/A | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | See Notes | 35 | - | Vendor Supplied | PRO-DAT-0020 CCI-DAT-1460 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
133 | TH00 | P02 | 0NDB | 10 | PI | CP | 522 |  | 22 | P020NDB10CP522 | Pressure Gauge | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B Inlet | Pressure | N/A | N/A | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | See Notes | 35 | - | Vendor Supplied | PRO-DAT-0020 CCI-DAT-1460 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
144 | TH00 | P02 | 0NDB | 10 | PI | CP | 523 |  | 33 | P020NDB10CP523 | Pressure Gauge | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B Outlet | Pressure | N/A | N/A | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | See Notes | 35 | - | Vendor Supplied | PRO-DAT-0020 CCI-DAT-1460 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
150 | TH00 | P02 | 0NDB | 10 | PI | CP | 532 |  | 39 | P020NDB10CP532 | Pressure Gauge | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C Inlet | Pressure | N/A | N/A | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | See Notes | 35 | - | Vendor Supplied | PRO-DAT-0020 CCI-DAT-1460 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
161 | TH00 | P02 | 0NDB | 10 | PI | CP | 533 |  | 50 | P020NDB10CP533 | Pressure Gauge | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C Outlet | Pressure | N/A | N/A | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | bar(g) | See Notes | 35 | - | Vendor Supplied | PRO-DAT-0020 CCI-DAT-1460 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
113 | TH00 | P02 | 0NDB | 10 | TE | CT | 010 |  | 2 | P020NDB10CT010 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A Inlet | Temperature | P020NDB10-BR021-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | °C | 0 to 250 | 123 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0026 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
122 | TH00 | P02 | 0NDB | 10 | TE | CT | 013 |  | 11 | P020NDB10CT013 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
123 | TH00 | P02 | 0NDB | 10 | TE | CT | 014 |  | 12 | P020NDB10CT014 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
124 | TH00 | P02 | 0NDB | 10 | TE | CT | 015 |  | 13 | P020NDB10CT015 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
125 | TH00 | P02 | 0NDB | 10 | TE | CT | 016 |  | 14 | P020NDB10CT016 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
126 | TH00 | P02 | 0NDB | 10 | TE | CT | 017 |  | 15 | P020NDB10CT017 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
131 | TH00 | P02 | 0NDB | 10 | TE | CT | 020 |  | 20 | P020NDB10CT020 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B Inlet | Temperature | P020NDB10-BR022-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | °C | 0 to 250 | 123 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0026 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
139 | TH00 | P02 | 0NDB | 10 | TE | CT | 023 |  | 28 | P020NDB10CT023 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
140 | TH00 | P02 | 0NDB | 10 | TE | CT | 024 |  | 29 | P020NDB10CT024 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
141 | TH00 | P02 | 0NDB | 10 | TE | CT | 025 |  | 30 | P020NDB10CT025 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
142 | TH00 | P02 | 0NDB | 10 | TE | CT | 026 |  | 31 | P020NDB10CT026 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
143 | TH00 | P02 | 0NDB | 10 | TE | CT | 027 |  | 32 | P020NDB10CT027 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
148 | TH00 | P02 | 0NDB | 10 | TE | CT | 030 |  | 37 | P020NDB10CT030 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C Inlet | Temperature | P020NDB10-BR023-400-CR1 | 400 | CR1 | SGW Re-injection | Full Vac | 45 | -5 | 143 | - | - | °C | 0 to 250 | 120 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0026 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0235SLAR1C2B1UAE065TBXW+114CM0160TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
156 | TH00 | P02 | 0NDB | 10 | TE | CT | 033 |  | 45 | P020NDB10CT033 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
157 | TH00 | P02 | 0NDB | 10 | TE | CT | 034 |  | 46 | P020NDB10CT034 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
158 | TH00 | P02 | 0NDB | 10 | TE | CT | 035 |  | 47 | P020NDB10CT035 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
159 | TH00 | P02 | 0NDB | 10 | TE | CT | 036 |  | 48 | P020NDB10CT036 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
160 | TH00 | P02 | 0NDB | 10 | TE | CT | 037 |  | 49 | P020NDB10CT037 | Temperature Element | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C | Temperature | N/A | N/A | CR1 | SGW Re-injection | N/A | N/A | -5 | 150 | - | - | °C | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
117 | TH00 | P02 | 0NDB | 10 | VXT | CY | 010 |  | 6 | P020NDB10CY010 | Vibration Transmitter | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A | Vibration | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
118 | TH00 | P02 | 0NDB | 10 | VYT | CY | 011 |  | 7 | P020NDB10CY011 | Vibration Transmitter | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A | Vibration | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
119 | TH00 | P02 | 0NDB | 10 | VXT | CY | 012 |  | 8 | P020NDB10CY012 | Vibration Transmitter | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A | Vibration | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
120 | TH00 | P02 | 0NDB | 10 | VYT | CY | 013 |  | 9 | P020NDB10CY013 | Vibration Transmitter | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A | Vibration | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
121 | TH00 | P02 | 0NDB | 10 | ST | CY | 014 |  | 10 | P020NDB10CY014 | Speed Indicator | Pump Station | Separated Water System | P020NDB10-AP010 | SGW Reinjection Pump A | Speed/Frequecny | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
134 | TH00 | P02 | 0NDB | 10 | VXT | CY | 020 |  | 23 | P020NDB10CY020 | Vibration Transmitter | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B | Vibration | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
135 | TH00 | P02 | 0NDB | 10 | VYT | CY | 021 |  | 24 | P020NDB10CY021 | Vibration Transmitter | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B | Vibration | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
136 | TH00 | P02 | 0NDB | 10 | VXT | CY | 022 |  | 25 | P020NDB10CY022 | Vibration Transmitter | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B | Vibration | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
137 | TH00 | P02 | 0NDB | 10 | VYT | CY | 023 |  | 26 | P020NDB10CY023 | Vibration Transmitter | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B | Vibration | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
138 | TH00 | P02 | 0NDB | 10 | ST | CY | 024 |  | 27 | P020NDB10CY024 | Speed Indicator | Pump Station | Separated Water System | P020NDB10-AP020 | SGW Reinjection Pump B | Speed/Frequecny | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
151 | TH00 | P02 | 0NDB | 10 | VXT | CY | 030 |  | 40 | P020NDB10CY030 | Vibration Transmitter | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C | Vibration | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
152 | TH00 | P02 | 0NDB | 10 | VYT | CY | 031 |  | 41 | P020NDB10CY031 | Vibration Transmitter | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C | Vibration | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
153 | TH00 | P02 | 0NDB | 10 | VXT | CY | 032 |  | 42 | P020NDB10CY032 | Vibration Transmitter | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C | Vibration | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
154 | TH00 | P02 | 0NDB | 10 | VYT | CY | 033 |  | 43 | P020NDB10CY033 | Vibration Transmitter | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C | Vibration | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
155 | TH00 | P02 | 0NDB | 10 | ST | CY | 034 |  | 44 | P020NDB10CY034 | Speed Indicator | Pump Station | Separated Water System | P020NDB10-AP030 | SGW Reinjection Pump C | Speed/Frequecny | N/A | N/A | CR1 | SGW Re-injection | atm | atm | -5 | 50 | - | - | mm/s | See Notes | Refer to Vendor | - | Vendor Supplied | PRO-DAT-0020 | PRO-PID-0026 | Note 1 |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
379 | TH00 | P02 | 0PCB | 20 | FIT | DF | 010 |  | 136 | P020PCB20CF010 | Flow Transmitter (Magnetic) | Pump Station | VSD Cooling Water System | S020PCB20-AP010 | Coolant Pump A Outlet | Flow | S020PCB20-BR021-50-S8 | 50 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | 0 | 720 | l/m | 0 to 720 | 707 | 0 to 720 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0044 | DN50 CL150 | 5.6 | Custom Controls | Rosemount | 8705TSA020C1W0G1B3Q4Q8+8732EMT2A2M4+ | 4500191995 | 2022-11-10
395 | TH00 | P02 | 0PCB | 20 | FIT | DF | 020 |  | 139 | P020PCB20CF020 | Flow Transmitter (Magnetic) | Pump Station | VSD Cooling Water System | S020PCB20-AP020 | Coolant Pump B Outlet | Flow | S020PCB20-BR022-50-S8 | 50 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | 0 | 720 | l/m | 0 to 720 | 707 | 0 to 720 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0044 | DN50 CL150 | 5.6 | Custom Controls | Rosemount | 8705TSA020C1W0G1B3Q4Q8+8732EMT2A2M4+ | 4500191995 | 2022-11-10
377 | TH00 | P02 | 0PCB | 20 | PIT | CP | 010 |  | 134 | P020PCB20CP010 | Pressure Indicating Transmitter | Pump Station | VSD Cooling Water System |  | Coolant Pumps Inlet | Pressure | S020PCB20-BR001-80-S8 | 80 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | bar(g) | -1 to 10.3 | 0.9 | 0 to 6 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0044 |  | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
380 | TH00 | P02 | 0PCB | 20 | PIT | CP | 540 |  | 137 | P020PCB20CP040 | Pressure Indicating Transmitter | Pump Station | VSD Cooling Water System |  | Coolant Pumps Outlet | Pressure | S020PCB20-BR030-80-S8 | 80 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | bar(g) | -1 to 10.3 | 5.82 | 0 to 6 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0044 |  | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
383 | TH00 | P02 | 0PCB | 20 | PI | CP | 510 |  | 140 | P020PCB20CP510 | Pressure Gauge | Pump Station | VSD Cooling Water System | S020PCB20-BB020 | Glycol Dosing System Vessel | Pressure | N/A | N/A | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | bar(g) | 0 to 10 | 0.9 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0044 |  | 3.2 | Wika | Wika | 72039938+14503369+ | 4500189704 | 2022-11-10
378 | TH00 | P02 | 0PCB | 20 | PI | CP | 520 |  | 135 | P020PCB20CP520 | Pressure Gauge | Pump Station | VSD Cooling Water System | S020PCB20-AP010 | Coolant Pump A Inlet | Pressure | S020PCB20-BR011-80-S8 | 80 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | bar(g) | 0 to 10 | 5.82 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0044 |  | 3.2 | Wika | Wika | 72039938+14503369+ | 4500189704 | 2022-11-10
381 | TH00 | P02 | 0PCB | 20 | PI | CP | 530 |  | 138 | P020PCB20CP530 | Pressure Gauge | Pump Station | VSD Cooling Water System | S020PCB20-AP020 | Coolant Pump B Inlet | Pressure | S020PCB20-BR012-80-S8 | 80 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | bar(g) | 0 to 10 | 5.82 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0044 |  | 3.2 | Wika | Wika | 72039938+14503369+ | 4500189704 | 2022-11-10
390 | TH00 | P02 | 0PCB | 20 | TE | CT | 010 |  | 147 | P020PCB20CT010 | Temperature Element | Pump Station | VSD Cooling Water System |  | Fin Fan Coolers Cooling Water | Temperature | P020PCB20-BR001-80-S8 | 80 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 250 | 30 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0046 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0135SLAR1C2B1UAE065TBXW+114CM0060TAC2SC075AQ35Q5Q8XW | 4500191995 | 2022-11-10
391 | TH00 | P02 | 0PCB | 20 | TE | CT | 011 |  | 148 | P020PCB20CT011 | Temperature Element | Pump Station | VSD Cooling Water System |  | Fin Fan Coolers Cooling Water | Temperature | P020PCB20-BR001-80-S8 | 80 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 250 | 30 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0046 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0135SLAR1C2B1UAE065TBXW+114CM0060TAC2SC075AQ35Q5Q8XW | 4500191995 | 2022-11-10
392 | TH00 | P02 | 0PCB | 20 | TE | CT | 012 |  | 149 | P020PCB20CT012 | Temperature Element | Pump Station | VSD Cooling Water System |  | Fin Fan Coolers Cooling Water | Temperature | P020PCB20-BR001-80-S8 | 80 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 250 | 30 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0046 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0135SLAR1C2B1UAE065TBXW+114CM0060TAC2SC075AQ35Q5Q8XW | 4500191995 | 2022-11-10
384 | TH00 | P02 | 0PCB | 22 | TE | DT | 011 |  | 141 | P020PCB22CT011 | Temperature Element | Pump Station | VSD Cooling Water System | P020PCB22-AC001 | SGW VSD A Cooling Water | Temperature | S020PCB22-BR051-50-S8 | 50 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 250 | 40 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0045 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW | 4500191995 | 2022-11-10
386 | TH00 | P02 | 0PCB | 22 | TE | DT | 012 |  | 143 | P020PCB22CT012 | Temperature Element | Pump Station | VSD Cooling Water System | P020PCB22-AC002 | SGW VSD B Cooling Water | Temperature | S020PCB22-BR052-50-S8 | 50 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 250 | 40 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0045 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW | 4500191995 | 2022-11-10
388 | TH00 | P02 | 0PCB | 22 | TE | DT | 013 |  | 145 | P020PCB22CT013 | Temperature Element | Pump Station | VSD Cooling Water System | P020PCB22-AC003 | SGW VSD C Cooling Water | Temperature | S020PCB22-BR053-50-S8 | 50 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 250 | 40 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0045 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW | 4500191995 | 2022-11-10
385 | TH00 | P02 | 0PCB | 22 | TE | DT | 021 |  | 142 | P020PCB22CT021 | Temperature Element | Pump Station | VSD Cooling Water System | P020PCB22-AC001 | SGW VSD A Cooling Water | Temperature |  | N/A | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 250 | 30 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0045 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0155SLAR1C2B1UAE065TBXW+114CM0080TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
387 | TH00 | P02 | 0PCB | 22 | TE | DT | 022 |  | 144 | P020PCB22CT022 | Temperature Element | Pump Station | VSD Cooling Water System | P020PCB22-AC002 | SGW VSD B Cooling Water | Temperature |  | N/A | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 250 | 30 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0045 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0155SLAR1C2B1UAE065TBXW+114CM0080TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
389 | TH00 | P02 | 0PCB | 22 | TE | DT | 023 |  | 146 | P020PCB22CT023 | Temperature Element | Pump Station | VSD Cooling Water System | P020PCB22-AC003 | SGW VSD C Cooling Water | Temperature |  | N/A | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 250 | 30 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0045 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0155SLAR1C2B1UAE065TBXW+114CM0080TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
| TH00 | P02 | 0PCB | 22 | TE | CT | 031 |  |  | P020PCB22CT031 | Temperature Element | Pump Station | VSD Cooling Water System | P020PCB22-AC001 | SGW VSD A Cooling Water Inlet | Temperature |  | 50 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 250 | 30 | - | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0045 | Note 7 New KKS Tag, old: P020PCB22CT031 | 5.9 | Custom Controls | Rosemount | 214CRWSMB1S4M0125SLAR1C2B1UAE065TBXW +114CM0050TAC2SC075AQ35Q5Q8XW | 4500197800 | 2023-03-20
| TH00 | P02 | 0PCB | 22 | TE | CT | 032 |  |  | P020PCB22CT032 | Temperature Element | Pump Station | VSD Cooling Water System | P020PCB22-AC002 | SGW VSD B Cooling Water Inlet | Temperature |  | 50 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 250 | 30 | - | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0045 | Note 7 New KKS Tag, old: P020PCB22CT032 | 5.9 | Custom Controls | Rosemount | 214CRWSMB1S4M0125SLAR1C2B1UAE065TBXW +114CM0050TAC2SC075AQ35Q5Q8XW | 4500197800 | 2023-03-20
| TH00 | P02 | 0PCB | 22 | TE | CT | 033 |  |  | P020PCB22CT033 | Temperature Element | Pump Station | VSD Cooling Water System | P020PCB22-AC003 | SGW VSD C Cooling Water Inlet | Temperature |  | 50 | S8 | VSD Cooling Water | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 250 | 30 | - | CCI-DET-2703 | CCI-DAT-1466 | PRO-PID-0045 | Note 7 New KKS Tag, old: P020PCB22CT033 | 5.9 | Custom Controls | Rosemount | 214CRWSMB1S4M0125SLAR1C2B1UAE065TBXW +114CM0050TAC2SC075AQ35Q5Q8XW | 4500197800 | 2023-03-20
393 | TH00 | P02 | 0QFB | 10 | PIT | CP | 010 |  | 150 | P020QFB10CP010 | Pressure Indicating Transmitter | Pump Station | Instrument Air System | P020QFB10-BB010 | Air Receiver A | Pressure | P020QFB10-BR013-50-OFFSPEC | 50 | SPECIAL | Compressed Air | Full Vac | 12 | -5 | 40 | - | - | bar(g) | -1 to 55 | 10 | 0 to 12 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0047 |  | 6.2 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
394 | TH00 | P02 | 0QFB | 10 | PIT | CP | 020 |  | 151 | P020QFB10CP020 | Pressure Indicating Transmitter | Pump Station | Instrument Air System | P020QFB10-BB020 / 21 | Air Receiver B1 & B2 | Pressure | P020QFB10-BR023-50-OFFSPEC | 50 | SPECIAL | Compressed Air | Full Vac | 12 | -5 | 40 | - | - | bar(g) | -1 to 55 | 10 | 0 to 12 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0047 |  | 6.2 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
395 | TH00 | P02 | 0QFB | 10 | PIT | CP | 030 |  | 152 | P020QFB10CP030 | Pressure Indicating Transmitter | Pump Station | Instrument Air System | P020QFB10-BB030 | Air Receiver C | Pressure | P020QFB10-BR033-50-OFFSPEC | 50 | SPECIAL | Compressed Air | Full Vac | 12 | -5 | 40 | - | - | bar(g) | -1 to 55 | 10 | 0 to 12 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0047 |  | 6.2 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
395.1 | TH00 | P02 | 0QFB | 10 | PIT | CP | 040 |  | 152.1 | P020QFB10CP040 | Pressure Indicating Transmitter | Pump Station | Instrument Air System | P020QFB10-BB040 | Air Receiver D | Pressure | P020QFB10-BR043-50-OFFSPEC | 50 | SPECIAL | Compressed Air | Full Vac | 12 | -5 | 40 | - | - | bar(g) | -1 to 55 | 10 | 0 to 12 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0047 |  | 6.2 | Custom Controls | Rosemount | 3051TG3A2B21BB4M4T1Q4Q8S5 c/w 0306RT22BA11 | 4500193144 | 2023-01-12
395.2 | TH00 | P02 | 0QFB | 10 | PIT | CP | 050 |  | 152.2 | P020QFB10CP050 | Pressure Indicating Transmitter | Pump Station | Instrument Air System | P020QFB10-BB050 | Air Receiver E | Pressure | P020QFB10-BR053-50-OFFSPEC | 50 | SPECIAL | Compressed Air | Full Vac | 12 | -5 | 40 | - | - | bar(g) | -1 to 55 | 10 | 0 to 12 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0047 |  | 6.2 | Custom Controls | Rosemount | 3051TG3A2B21BB4M4T1Q4Q8S5 c/w 0306RT22BA11 | 4500193144 | 2023-01-12
393.1 | TH00 | P02 | 0QFB | 10 | PI | CP | 510 |  | 150 | P020QFB10CP511 | Pressure Gauge | Pump Station | Instrument Air System | P020QFB10-BB010 | Air Receiver A | Pressure | P020QFB10-BR013-50-S6 | 50 | S6 | Compressed Air | Full Vac | 12 | -5 | 40 | - | - | bar(g) | -1 to 55 | 10 | 0 to 16 | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0047 |  | 6.3 | Wika | Wika | 72039879+14298395 | 4500196708 | 2023-01-09
394.1 | TH00 | P02 | 0QFB | 10 | PI | CP | 520 |  | 151 | P020QFB10CP521 | Pressure Gauge | Pump Station | Instrument Air System | P020QFB10-BB020 | Air Receiver B1 | Pressure | P020QFB10-BR023-50-S6 | 50 | S6 | Compressed Air | Full Vac | 12 | -5 | 40 | - | - | bar(g) | -1 to 55 | 10 | 0 to 16 | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0047 |  | 6.3 | Wika | Wika | 72039879+14298395 | 4500196708 | 2023-01-09
395.1 | TH00 | P02 | 0QFB | 10 | PI | CP | 530 |  | 152 | P020QFB10CP531 | Pressure Gauge | Pump Station | Instrument Air System | P020QFB10-BB030 | Air Receiver C | Pressure | P020QFB10-BR033-50-S6 | 50 | S6 | Compressed Air | Full Vac | 12 | -5 | 40 | - | - | bar(g) | -1 to 55 | 10 | 0 to 16 | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0047 |  | 6.3 | Wika | Wika | 72039879+14298395 | 4500196708 | 2023-01-09
395.2 | TH00 | P02 | 0QFB | 10 | PI | CP | 540 |  | 152.2 | P020QFB10CP541 | Pressure Gauge | Pump Station | Instrument Air System | P020QFB10-BB030 | Air Receiver D | Pressure | P020QFB10-BR033-50-S6 | 50 | S6 | Compressed Air | Full Vac | 12 | -5 | 40 | - | - | bar(g) | -1 to 55 | 10 | 0 to 16 | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0047 |  | 6.3 | Wika | Wika | 72039879+14298395 | 4500196708 | 2023-01-09
395.2 | TH00 | P02 | 0QFB | 10 | PI | CP | 550 |  | 152.2 | P020QFB10CP551 | Pressure Gauge | Pump Station | Instrument Air System | P020QFB10-BB030 | Air Receiver E | Pressure | P020QFB10-BR033-50-S6 | 50 | S6 | Compressed Air | Full Vac | 12 | -5 | 40 | - | - | bar(g) | -1 to 55 | 10 | 0 to 16 | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0047 |  | 6.3 | Wika | Wika | 72039879+14298395 | 4500196708 | 2023-01-09
395.3 | TH00 | P02 | 0QFB | 10 | PI | CP | 650 |  | 152.3 | P020QFB10CP523 | Pressure Gauge | Pump Station | Instrument Air System | P020QFB10-BB030 | Air Receiver B2 | Pressure | P020QFB10-BR033-50-S6 | 50 | S6 | Compressed Air | Full Vac | 12 | -5 | 40 | - | - | bar(g) | -1 to 55 | 10 | 0 to 16 | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0047 |  | 6.3 | Wika | Wika | 72039879+14298395 | 4500196708 | 2023-01-09
400 | TH00 | S02 | 0GAC | 10 | LT | CL | 010 |  | 175 | S020GAC10CL010 | Level Transmitter (Radar) | Separation Plant | Raw Water System | P020GAC10-BB010 | Raw Water Tank 1 | Level | N/A | N/A | S8 | Raw Water | Full Vac | 10 | -5 | 75 | - | - | mm | See notes | N/A | TBC | Nozzle Mount PRO-DAT-0088 | CCI-DAT-1468 | PRO-PID-0051 | Tank manufacturer to finalise tank height. 2"/DN50 CL150 | 3.2 | Custom Controls | Rosemount | 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8+751AM1NAB+ | 4500191995 | 2022-11-10
398 | TH00 | S02 | 0GAC | 10 | LT | CL | 011 |  | 173 | S020GAC10CL011 | Level Transmitter (Radar) | Separation Plant | Raw Water System | P020GAC10-BB020 | Raw Water Tank 2 | Level | N/A | N/A | S8 | Raw Water | Full Vac | 10 | -5 | 75 | - | - | mm | See notes | N/A | TBC | Nozzle Mount PRO-DAT-0088 | CCI-DAT-1468 | PRO-PID-0051 | Tank manufacturer to finalise tank height. 2"/DN50 CL150 | 3.2 | Custom Controls | Rosemount | 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8+751AM1NAB+ | 4500191995 | 2022-11-10
401 | TH00 | S02 | 0GAC | 10 | LG | CL | 020 |  | 176 | S020GAC10CL020 | Level Gauge | Separation Plant | Raw Water System | P020GAC10-BB010 | Raw Water Tank 1 | Level | N/A | 50 | S8 | Raw Water | Full Vac | 10 | -5 | 75 | - | - | mm | - | N/A | Refer to Notes | CCI-DET-2705 | CCI-DAT-1471 PRO-DAT-0088 | PRO-PID-0051 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
399 | TH00 | S02 | 0GAC | 10 | LG | CL | 021 |  | 174 | S020GAC10CL021 | Level Gauge | Separation Plant | Raw Water System | P020GAC10-BB020 | Raw Water Tank 2 | Level | N/A | 50 | S8 | Raw Water | Full Vac | 10 | -5 | 75 | - | - | mm | - | N/A | Refer to Notes | CCI-DET-2705 | CCI-DAT-1471 PRO-DAT-0088 | PRO-PID-0051 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
397 | TH00 | S02 | 0GAC | 10 | PDIT | DP | 001 |  | 172 | S020GAC10CP001 | Pressure Differential Transmitter | Separation Plant | Raw Water System | - | Raw Water Supply Line | Pressure | S020GAC10-BR013-50-S8 | 50 | S8 | Raw Water | Full Vac | 10 | -5 | 75 | - | - | bar(g) | 0 to 20 | 3.49 | 0 to 4 | CCI-DET-2702 | CCI-DAT-1462 | PRO-PID-0051 |  | 3.2 | Custom Controls | Rosemount | 2051CD4A02A1BS5M4Q4 c/w 0305RC52B11B4++ | 4500191995 | 2022-11-10
396 | TH00 | S02 | 0GAC | 10 | PIT | CP | 002 |  | 171 | S020GAC10CP002 | Pressure Indicating Transmitter | Separation Plant | Raw Water System | - | Raw Water Supply Line | Pressure | S020GAC10-BR001-50-S8 | 100 | S8 | Raw Water | Full Vac | 10 | -5 | 75 | - | - | bar(g) | -1 to 10.3 | 2.98 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0051 |  | 6.2 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
[9 empty] | 177 | S020GAC21CP020 | Pressure Indicating Transmitter | Separation Plant | Raw Water System | - | Raw Water Supply Line | Pressure | P020GAC21-BR050-50-S8 | 50 | S8 | Raw Water | Full Vac | 10 | -5 | 75 | - | - | bar(g) | -1 to 10.3 | 2.98 | 0 to 8 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0051 |  | 6.8 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
420 | TH00 | S02 | 0GAC | 22 | FI | CF | 501 |  | 196 | S020GAC22CF501 | Flow Indicator | Separation Plant | Raw Water System | - | HP SGW pH Monitoring Skid | Flow | S020GAC22-BR061-25-S8 | 25 | S8 | SGW Condensate | Full Vac | 10 | -5 | 75 | 0 | 5 l/m | l/m | Refer to Specification | Refer to Specification | - | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0101 | Rotameter Type Note 1 | 3.5 | Wika | Brooks | 72040298 WR1330, BRO-2540A5L59SS-NL | 4500193000 | 2022-11-25
426 | TH00 | S02 | 0GAC | 22 | FI | CF | 510 |  | 202 | S020GAC22CF510 | Flow Indicator | Separation Plant | Raw Water System | - | HP SGW pH Monitoring Skid | Flow | S020GAC22-BR062-25-S8 | 25 | S8 | SGW Condensate | Full Vac | 10 | -5 | 75 | 0 | 5 l/m | l/m | Refer to Specification | Refer to Specification | - | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0101 | Rotameter Type Note 1 | 3.5 | Wika | Brooks | 72040298 WR1330, BRO-2540A5L59SS-NL | 4500193000 | 2022-11-25
403 | TH00 | S02 | 0GAC | 22 | FI | CF | 520 |  | 179 | S020GAC22CF520 | Flow Indicator | Separation Plant | Raw Water System | - | LP SGW pH Monitoring Skid | Flow | S020GAC22-BR081-25-S8 | 25 | S8 | Raw Water | Full Vac | 10 | -5 | 75 | 0 | 5 l/m | l/m | Refer to Specification | Refer to Specification | - | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Rotameter Type Note 1 | 3.5 | Wika | Brooks | 72040298 WR1330, BRO-2540A5L59SS-NL | 4500193000 | 2022-11-25
407 | TH00 | S02 | 0GAC | 22 | FI | CF | 530 |  | 183 | S020GAC22CF530 | Flow Indicator | Separation Plant | Raw Water System | - | LP SGW pH Monitoring Skid | Flow | S020GAC22-BR082-25-S8 | 25 | S8 | Raw Water | Full Vac | 10 | -5 | 75 | 0 | 5 l/m | l/m | Refer to Specification | Refer to Specification | - | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Rotameter Type Note 1 | 3.5 | Wika | Brooks | 72040298 WR1330, BRO-2540A5L59SS-NL | 4500193000 | 2022-11-25
411 | TH00 | S02 | 0GAC | 22 | FI | CF | 540 |  | 187 | S020GAC22CF540 | Flow Indicator | Separation Plant | Raw Water System | - | LP SGW pH Monitoring Skid | Flow | S020GAC22-BR083-25-S8 | 25 | S8 | Raw Water | Full Vac | 10 | -5 | 75 | 0 | 5 l/m | l/m | Refer to Specification | Refer to Specification | - | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Rotameter Type Note 1 | 3.5 | Wika | Brooks | 72040298 WR1330, BRO-2540A5L59SS-NL | 4500193000 | 2022-11-25
415 | TH00 | S02 | 0GAC | 22 | FI | CF | 550 |  | 191 | S020GAC22CF550 | Flow Indicator | Separation Plant | Raw Water System | - | LP SGW pH Monitoring Skid | Flow | S020GAC22-BR084-25-S8 | 25 | S8 | Raw Water | Full Vac | 10 | -5 | 75 | 0 | 5 l/m | l/m | Refer to Specification | Refer to Specification | - | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Rotameter Type Note 1 | 3.5 | Wika | Brooks | 72040298 WR1330, BRO-2540A5L59SS-NL | 4500193000 | 2022-11-25
| TH00 | S02 | 0GBK | 10 | LIT | CL | 10 |  |  | S020GBK10CL010 | Level Transmitter (Radar) | Separation Plant | Calcite Inhibitor Tank | S020QCM30-AP010 | Calcite Inhibitor Tank | Level | N/A | N/A | N/A | Calcite Inhibitor | atm | atm | -5 | 50 | - | - | mm | 0 to 2500 | N/A | 0 to 2500 | CCI-DET-2706 | CCI-DAT-1468 | PRO-PID-0053 | Flange mount | 4.7 | Instrumatics | Vega | PS21.XXXXXGMHB+GFL-PLUS.GG+DIS82.IXHKIMACX | 4500193055 4500195517 | 2023-01-13
| TH00 | S02 | 0GBK | 10 | LIT | CL | 11 |  |  | S020GBK10CL011 | Level Transmitter (Radar) | Separation Plant | Calcite Inhibitor Sump | S020QCM30-AP010 | Calcite Inhibitor Sump | Level | N/A | N/A | N/A | Calcite Inhibitor | atm | atm | -5 | 50 | - | - | mm | 0 to 1000 | N/A | 0 to 1000 | CCI-DET-2706 | CCI-DAT-1468 | PRO-PID-0053 | SPARE | 7.7 | Instrumatics | Vega | PS21.XXXXXGMHB+MBA.BB | 4500193055 | 2023-01-13
| TH00 | S02 | 0GBK | 10 | LIT | CL | 20 |  |  | S020GBK10CL020 | Level Gauge | Separation Plant | Calcite Inhibitor Tank | S020QCM30-AP010 | Calcite Inhibitor Tank | Level | N/A | 25 | N/A | Calcite Inhibitor | atm | atm | -5 | 50 | - | - | mm | 0 to 2500 | N/A | 0 to 2500 | CCI-DET-2706 | CCI-DAT-1468 | PRO-PID-0053 | Supplied with tank | 2.2 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0GBK | 10 | HS | GS | 10 |  |  | S020GBK10GS010 | Motor Starter (Local) | Separation Plant | Calcite Inhibitor Tank | S020GBK10AP010 | Calcite Inhibitor Load Out Pump | Power | N/A | N/A | N/A | Calcite Inhibitor | - | - | - | - | - | - | - | - | N/A | - | - | - | PRO-PID-0053 |  | 2.3 | Corys | Schneider | 56DOL9 Starter + TELE LRD12 Overload | 4500193425
327 | TH00 | S02 | 0GKA | 10 | LIT | CL | 010 |  | 161 | S020GKA10CL010 | Level Transmitter (Radar) | Separation Plant | Potable Water System | S020GKA10-BB010 | Potable Water Tank 1 | Level | N/A | N/A | S8 | Potable Water | Full Vac | 10 | -5 | 75 | - | - | mm | See notes | N/A | TBC | Nozzle Mount PRO-DAT-0074 | CCI-DAT-1468 | PRO-PID-0040 | Tank manufacturer to finalise tank height. 2"/DN50 CL150 | 3.2 | Custom Controls | Rosemount | 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8+751AM1NAB+ | 4500191995 | 2022-11-10
329 | TH00 | S02 | 0GKA | 10 | LIT | CL | 011 |  | 163 | S020GKA10CL011 | Level Transmitter (Radar) | Separation Plant | Potable Water System | S020GKA10-BB020 | Potable Water Tank 2 | Level | N/A | N/A | S8 | Potable Water | Full Vac | 10 | -5 | 75 | - | - | mm | See notes | N/A | TBC | Nozzle Mount PRO-DAT-0074 | CCI-DAT-1468 | PRO-PID-0040 | Tank manufacturer to finalise tank height. 2"/DN50 CL150 | 3.2 | Custom Controls | Rosemount | 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8+751AM1NAB+ | 4500191995 | 2022-11-10
328 | TH00 | S02 | 0GKA | 10 | LG | CL | 020 |  | 162 | S020GKA10CL020 | Level Gauge | Separation Plant | Potable Water System | S020GKA10-BB010 | Potable Water Tank 1 | Level | N/A | 50 | S8 | Potable Water | Full Vac | 10 | -5 | 75 | - | - | mm | - | N/A | Refer to Notes | CCI-DET-2705 | CCI-DAT-1471 PRO-DAT-0074 | PRO-PID-0040 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
330 | TH00 | S02 | 0GKA | 10 | LG | CL | 021 |  | 164 | S020GKA10CL021 | Level Gauge | Separation Plant | Potable Water System | S020GKA10-BB020 | Potable Water Tank 2 | Level | N/A | 50 | S8 | Potable Water | Full Vac | 10 | -5 | 75 | - | - | mm | - | N/A | Refer to Notes | CCI-DET-2705 | CCI-DAT-1471 PRO-DAT-0074 | PRO-PID-0040 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. |  | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
333 | TH00 | S02 | 0GKA | 20 | FSH | CF | 191 |  | 167 | S020GKA21CF191 | Flow Switch | Separation Plant | Potable Water System | - | Acid Dosing Emergency Eye Wash | Flow | S020GKA20-BR051-50-S8 | 50 | S8 | Potable Water | Full Vac | 10 | -5 | 75 | 0 | 2 | kg/s | 0 to 2 | >1.5 | N/A | CCI-DET-2709 | CCI-DAT-1476 | PRO-PID-0040 |  | 6.1 | Wika | Wika | 72039911++ | 4500189704 | 2022-11-10
334 | TH00 | S02 | 0GKA | 20 | FSH | CF | 192 |  | 168 | S020GKA21CF192 | Flow Switch | Separation Plant | Potable Water System | - | Acid Dosing Emergency Eye Wash | Flow | S020GKA20-BR051-50-S8 | 50 | S8 | Potable Water | Full Vac | 10 | -5 | 75 | 0 | 2 | kg/s | 0 to 2 | >1.5 | N/A | CCI-DET-2709 | CCI-DAT-1476 | PRO-PID-0040 |  | 6.1 | Wika | Wika | 72039911++ | 4500189704 | 2022-11-10
335 | TH00 | S02 | 0GKA | 20 | FSH | CF | 193 |  | 169 | S020GKA21CF193 | Flow Switch | Separation Plant | Potable Water System | - | Acid Dosing Emergency Eye Wash | Flow | S020GKA20-BR051-50-S8 | 50 | S8 | Potable Water | Full Vac | 10 | -5 | 75 | 0 | 2 | kg/s | 0 to 2 | >1.5 | N/A | CCI-DET-2709 | CCI-DAT-1476 | PRO-PID-0040 |  | 6.1 | Wika | Wika | 72039911++ | 4500189704 | 2022-11-10
336 | TH00 | S02 | 0GKA | 20 | FSH | CF | 194 |  | 170 | S020GKA21CF194 | Flow Switch | Separation Plant | Potable Water System | - | Separation Station Battery Room Eye Wash | Flow | S020GKA20-BR052-50-S8 | 50 | S8 | Potable Water | Full Vac | 10 | -5 | 75 | 0 | 4 | kg/s | 0 to 4 | >1.5 | N/A | CCI-DET-2709 | CCI-DAT-1476 | PRO-PID-0040 |  | 6.1 | Wika | Wika | 72039911++ | 4500189704 | 2022-11-10
332 | TH00 | S02 | 0GKA | 20 | FSH | CF | 195 |  | 166 | S020GKA21CF195 | Flow Switch | Pump Station | Potable Water System | - | SGW Pump Building Battery Room Eye Wash | Flow | S020GKA20-BR053-50-S8 | 50 | S8 | Potable Water | Full Vac | 10 | -5 | 75 | 0 | 3 | kg/s | 0 to 3 | >1.5 | N/A | CCI-DET-2709 | CCI-DAT-1476 | PRO-PID-0040 |  | 6.1 | Wika | Wika | 72039911++ | 4500189704 | 2022-11-10
| TH00 | S02 | 0GKA | 20 | FSH | CF | 196 |  |  | S020GKA21CF196 | Flow Switch | Pump Station | Potable Water System | - | Acid Tanker Load-in Pad | Flow | S020GKA20-BR053-50-S8 | 50 | S8 | Potable Water | Full Vac | 10 | -5 | 75 | 0 | 3 | kg/s | 0 to 3 | >1.5 | N/A | CCI-DET-2709 | CCI-DAT-1476 | PRO-PID-0040 |  | 7.3 | Wika | Wika | 72039911++ | 4500200070 | 2023-05-22
331 | TH00 | S02 | 0GKA | 20 | PI | CP | 520 |  | 165 | S020GKA20CP520 | Pressure Gauge | Separation Plant | Potable Water System | - | Potable Water to Separation Plant | Pressure | S020GKA20-BR043-50-S8 | 50 | S8 | Potable Water | Full Vac | 10 | -5 | 75 | - | - | bar(g) | 0 to 25 | 3.14 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0040 |  | 3.2 | Wika | Wika | 72039882+14503369+ | 4500189704 | 2022-11-10
| TH00 | S02 | 0GWA | 10 | FIT | CF | 010 |  |  | S020GWA11CF010 | Flow Transmitter (Magnetic) | Separation Plant | Acid Dosing Seal Water |  | Acid Dosing System | Pressure | [10 empty] | 0 |  |  | 0 |  |  | PRO-PID-0055 | Was S020GWA10CF010 | 4.9 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0GWA | 10 | FIT | CF | 020 |  |  | S020GWA11CF020 | Flow Transmitter (Magnetic) | Separation Plant | Acid Dosing Seal Water |  | Acid Dosing System | Pressure | [10 empty] | 0 |  |  | 0 |  |  | PRO-PID-0055 | Was S020GWA10CF020 | 4.9 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0GWA | 10 | LS | CL | 310 |  |  | S020GWA10CL310 | Level Switch | Separation Plant | Acid Dosing Seal Water |  | Acid Dosing System | Level | [10 empty] | 0 |  |  | 0 |  |  | PRO-PID-0055 | Was S020GWA10CL310 | 4.9 | Instrumatics | Vega | P21.XXXXXABMIB | 4500196706 | 2022-12-19
| TH00 | S02 | 0GWA | 10 | TIT |  |  |  |  | S020GWA10CT010 | Temperature Indicating Transmitter | Separation Plant | Acid Dosing Seal Water |  | Acid Dosing System | Temperature |  | 25 | S8 | Seal Water | [6 empty] | °C | 0 to 250 | 123 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0055 | Replaced Upgrade Transient Protection 00644-4538-0101 | 7.4 | Custom Controls | Rosemount | 644HANAJ5M5Q4+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAA2SC075AQ35Q5Q8XW | 4500200505 | 644-25/05/23 214 ETA 15/06/23
| TH00 | S02 | 0GWA | 10 | TIT |  |  |  |  | S020GWA10CT020 | Temperature Indicating Transmitter | Separation Plant | Acid Dosing Seal Water |  | Acid Dosing System | Temperature |  | 25 | S8 | Seal Water | [6 empty] | °C | 0 to 250 | 123 | 0 to 250 | CCI-DET-2703 | CCI-DAT-1465 | PRO-PID-0055 | Replaced Upgrade Transient Protection 00644-4538-0101 | 7.4 | Custom Controls | Rosemount | 644HANAJ5M5Q4+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAA2SC075AQ35Q5Q8XW | 4500200505 | 644-25/05/23 214 ETA 15/06/23
| TH00 | S02 | 0GWA | 10 | PIT | CP | 010 |  |  | S020GWA12CP010 | Pressure Indicating Transmitter | Separation Plant | Acid Dosing Seal Water |  | Acid Dosing System | Pressure | [10 empty] | 0 |  |  | 0 |  |  | PRO-PID-0055 | Was S020GWA10CP010 | 6.2 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0GWA | 10 | PDIT | CP | 310 |  |  | S020GWA11CP510 | Pressure Differential Transmitter | Separation Plant | Acid Dosing Seal Water |  | Acid Dosing System | Pressure | [10 empty] | 0 |  |  | 0 |  |  | PRO-PID-0055 | Was S020GWA10CP310 | 4.9 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0GWA | 10 | TIT | CT | 010 |  |  | S020GWA12CT010 | Temperature Indicating Transmitter | Separation Plant | Acid Dosing Seal Water |  | Acid Dosing System | Temperature | [10 empty] | 0 |  |  | 0 |  |  | PRO-PID-0055 | Was S020GWA10CT010 | 4.9 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
64 | TH00 | S02 | 0LCE | 10 | FIT | DF | 010 |  | 84 | S020LCE10CF010 | Flow Transmitter (Orifice Flow) | Separation Plant | Process Water System | S020LCE10-AA110 | HP Steam Scrubbing Wash Water FCV | Flow | S020LCE10-BR010-40-S4 | 40 | S4 | High Temperature Wash Water | Full Vac | 49.6 | -5 | 240 | 0 | 18 | tph | 0 to 18 | 7.6 | 0 to 18 | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0018 | Note 3, Note 8 | 6.3 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1195F015A3S1184CBCG2+ | 4500191995 | 2023-04-19
72 | TH00 | S02 | 0LCE | 10 | FT | DF | 020 |  | 93 | S020LCE10CF020 | Flow Transmitter (Orifice Flow) | Separation Plant | Process Water System | S020LCE10-AA120 | IP Steam Scrubbing Wash Water FCV | Flow | S020LCE10-BR020-40-S4 | 40 | S4 | High Temperature Wash Water | Full Vac | 49.6 | -5 | 240 | 0 | 7.2 | tph | 0 to 7.2 | 2.2 | 0 to 7.2 | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0020 | Note 3, Note 8 | 5.6 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1195F015A3S1184CBCG2+ | 4500191995 | 2023-02-13
84 | TH00 | S02 | 0LCE | 10 | FT | DF | 030 |  | 105 | S020LCE10CF030 | Flow Transmitter (Orifice Flow) | Separation Plant | Process Water System | S020LCE10-AA130 | LP Steam Scrubbing A Wash Water FCV | Flow | S020LCE10-BR030-40-S4 | 40 | S4 | High Temperature Wash Water | Full Vac | 49.6 | -5 | 240 | 0 | 7.2 | tph | 0 to 7.2 | 1.8 | 0 to 7.2 | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0022 | Note 3, Note 8 | 5.6 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1195F015A3S1184CBCG2+ | 4500191995 | 2023-02-13
98 | TH00 | S02 | 0LCE | 10 | FT | DF | 040 |  | 119 | S020LCE10CF040 | Flow Transmitter (Orifice Flow) | Separation Plant | Process Water System | S020LCE10-AA140 | LP Steam Scrubbing B Wash Water FCV | Flow | S020LCE10-BR040-40-S4 | 40 | S4 | High Temperature Wash Water | Full Vac | 49.6 | -5 | 240 | 0 | 7.2 | tph | 0 to 7.2 | 1.8 | 0 to 7.2 | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0024 | Note 3, Note 8 | 5.6 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1195F015A3S1184CBCG2+ | 4500191995 | 2023-02-13
65 | TH00 | S02 | 0LCE | 10 | PI | CP | 510 |  | 85 | S020LCE10CP510 | Pressure Gauge | Separation Plant | Process Water System | S020LCE10-AA110 | HP Steam Scrubbing Wash Water FCV | Pressure | S020LCE10-BR010-40-S4 | 40 | S4 | High Temperature Wash Water | Full Vac | 30 | -5 | 215 | - | - | bar(g) | 0 to 60 | 16.72 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0018 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
73 | TH00 | S02 | 0LCE | 10 | PI | CP | 520 |  | 94 | S020LCE10CP520 | Pressure Gauge | Separation Plant | Process Water System | S020LCE10-AA120 | IP Steam Scrubbing Wash Water FCV | Pressure | S020LCE10-BR020-40-S4 | 40 | S4 | High Temperature Wash Water | Full Vac | 30 | -5 | 215 | - | - | bar(g) | 0 to 60 | 8.78 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0020 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
91 | TH00 | S02 | 0LCE | 10 | PI | CP | 530 |  | 112 | S020LCE10CP530 | Pressure Gauge | Separation Plant | Process Water System | S020LCE10-AA130 | LP Steam Scrubbing A Wash Water FCV | Pressure | S020LCE10-BR030-40-S4 | 40 | S4 | High Temperature Wash Water | Full Vac | 30 | -5 | 215 | - | - | bar(g) | 0 to 60 | 1.16 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0022 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
99 | TH00 | S02 | 0LCE | 10 | PI | CP | 540 |  | 120 | S020LCE10CP540 | Pressure Gauge | Separation Plant | Process Water System | S020LCE10-AA140 | LP Steam Scrubbing B Wash Water FCV | Pressure | S020LCE10-BR040-40-S4 | 40 | S4 | High Temperature Wash Water | Full Vac | 30 | -5 | 215 | - | - | bar(g) | 0 to 60 | 1.16 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0024 |  | 3.2 | Wika | Wika | 72039876+14503369+0731277 | 4500189704 | 2022-11-10
| TH00 | S02 | 0LCE | 20 | LIT | CL | 10 |  |  | S020LCE20CL010 | Level Transmitter (Radar) | Separation Plant | Deoxygenated Tank 1 | S020QCM30-AP010 | Deoxygenated Tank 1 | Level | N/A | N/A | N/A | DeOxygenated Water | atm | atm | -5 | 50 | - | - | mm | 0 to 3125 | N/A | 0 to 3125 | CCI-DET-2706 | CCI-DAT-1468 | PRO-PID-0053 | Flange mount | 5.6 | Instrumatics | Vega | PS21.XXXXXGMHB+GFL-PLUS.GG | 4500193055 | 2023-01-13
| TH00 | S02 | 0LCE | 20 | LIT | CL | 11 |  |  | S020LCE20CL011 | Level Transmitter (Radar) | Separation Plant | Deoxygenated Tank 2 | S020QCM30-AP010 | Deoxygenated Tank 2 | Level | N/A | N/A | N/A | DeOxygenated Water | atm | atm | -5 | 50 | - | - | mm | 0 to 3125 | N/A | 0 to 3125 | CCI-DET-2706 | CCI-DAT-1468 | PRO-PID-0053 | Flange mount | 5.6 | Instrumatics | Vega | PS21.XXXXXGMHB+GFL-PLUS.GG | 4500193055 | 2023-01-13
| TH00 | S02 | 0LCE | 20 | LIT | CL | 20 |  |  | S020LCE20CL020 | Level Gauge | Separation Plant | Deoxygenated Tank 1 | S020QCM30-AP010 | Deoxygenated Tank 1 | Level | N/A | 25 | N/A | DeOxygenated Water | atm | atm | -5 | 50 | - | - | mm | 0 to 3125 | N/A | 0 to 3125 | CCI-DET-2706 | CCI-DAT-1468 | PRO-PID-0053 | Supplied with tank | 2.2 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0LCE | 20 | LIT | CL | 21 |  |  | S020LCE20CL021 | Level Gauge | Separation Plant | Deoxygenated Tank 2 | S020QCM30-AP010 | Deoxygenated Tank 2 | Level | N/A | 25 | N/A | DeOxygenated Water | atm | atm | -5 | 50 | - | - | mm | 0 to 3125 | N/A | 0 to 3125 | CCI-DET-2706 | CCI-DAT-1468 | PRO-PID-0053 | Supplied with tank | 2.2 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
15 | TH00 | S02 | 0LFC | 10 | TE | CT | 001 |  | 15 | L050NDA10CT001 | Temperature Element | Separation Plant | Common Steam/Water Dump System | L050NDA10-AA191 | TH12 Two Phase Rupture Discs | Temperature | S020LFC10-BR501-500-CH1 | 500 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 226.1 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0011 | Note 7 New KKS Tag, old: S020LFC10CT001 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
14 | TH00 | S02 | 0LFC | 10 | TE | CT | 002 |  | 14 | L050NDA10CT002 | Temperature Element | Separation Plant | Common Steam/Water Dump System | L050NDA10-AA192 | TH12 Two Phase Rupture Discs | Temperature | S020LFC10-BR511-500-CH1 | 500 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 226.1 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0011 | Note 7 New KKS Tag, old: S020LFC10CT002 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
13 | TH00 | S02 | 0LFC | 10 | TE | CT | 003 |  | 13 | L050NDA10CT003 | Temperature Element | Separation Plant | Common Steam/Water Dump System | L050NDA10-AA193 | TH12 Two Phase Rupture Discs | Temperature | S020LFC10-BR521-500-CH1 | 500 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 226.1 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0011 | Note 7 New KKS Tag, old: S020LFC10CT003 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
9 | TH00 | S02 | 0LFC | 10 | TE | CT | 011 |  | 9 | L060NDA10CT011 | Temperature Element | Separation Plant | Common Steam/Water Dump System | L060NDA10-AA191 | TH28 Two Phase Rupture Discs | Temperature | S020LFC10-BR502-500-CH1 | 500 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 226.1 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0011 | Note 7 New KKS Tag, old: S020LFC10CT011 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
8 | TH00 | S02 | 0LFC | 10 | TE | CT | 012 |  | 8 | L060NDA10CT012 | Temperature Element | Separation Plant | Common Steam/Water Dump System | L060NDA10-AA192 | TH28 Two Phase Rupture Discs | Temperature | S020LFC10-BR512-500-CH1 | 500 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 226.1 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0011 | Note 7 New KKS Tag, old: S020LFC10CT012 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
7 | TH00 | S02 | 0LFC | 10 | TE | CT | 013 |  | 7 | L060NDA10CT013 | Temperature Element | Separation Plant | Common Steam/Water Dump System | L060NDA10-AA193 | TH28 Two Phase Rupture Discs | Temperature | S020LFC10-BR522-500-CH1 | 500 | CH1 | HP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 226.1 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0011 | Note 7 New KKS Tag, old: S020LFC10CT013 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
3 | TH00 | S02 | 0LFC | 10 | TE | CT | 021 |  | 3 | L070NDA10CT021 | Temperature Element | Separation Plant | Common Steam/Water Dump System | L070NDA10-AA191 | TH26 Two Phase Rupture Discs | Temperature | S020LFC10-BR503-500-CH1 | 500 | CH1 | LP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 226.1 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0011 | Note 7 New KKS Tag, old: S020LFC10CT021 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
2 | TH00 | S02 | 0LFC | 10 | TE | CT | 022 |  | 2 | L070NDA10CT022 | Temperature Element | Separation Plant | Common Steam/Water Dump System | L070NDA10-AA192 | TH26 Two Phase Rupture Discs | Temperature | S020LFC10-BR513-500-CH1 | 500 | CH1 | LP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 226.1 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0011 | Note 7 New KKS Tag, old: S020LFC10CT022 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
1 | TH00 | S02 | 0LFC | 10 | TE | CT | 023 |  | 1 | L070NDA10CT023 | Temperature Element | Separation Plant | Common Steam/Water Dump System | L070NDA10-AA193 | TH26 Two Phase Rupture Discs | Temperature | S020LFC10-BR523-500-CH1 | 500 | CH1 | LP Two Phase | Full Vac | 34 | -5 | 243 | - | - | °C | 0 to 250 | 226.1 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0011 | Note 7 New KKS Tag, old: S020LFC10CT023 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
58 | TH00 | S02 | 0LFC | 10 | TE | CT | 041 |  | 78 | S020NAA10CT041 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA10-AA191 | HP Steam Scrubbing Rupture Disc | Temperature | S020LFC10-BR541-500-CH3 | 500 | CH3 | HP Steam (Noise Attenuation) | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 250 | 215 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0018 | Note 7 New KKS Tag, old: S020LFC10CT041 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
59 | TH00 | S02 | 0LFC | 10 | TE | CT | 042 |  | 79 | S020NAA10CT042 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA10-AA192 | HP Steam Scrubbing Rupture Disc | Temperature | S020LFC10-BR542-500-CH3 | 500 | CH3 | HP Steam (Noise Attenuation) | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 250 | 215 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0018 | Note 7 New KKS Tag, old: S020LFC10CT042 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
60 | TH00 | S02 | 0LFC | 10 | TE | CT | 043 |  | 80 | S020NAA10CT043 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA10-AA193 | HP Steam Scrubbing Rupture Disc | Temperature | S020LFC10-BR543-500-CH3 | 500 | CH3 | HP Steam (Noise Attenuation) | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 250 | 215 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0018 | Note 7 New KKS Tag, old: S020LFC10CT043 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
61 | TH00 | S02 | 0LFC | 10 | TE | CT | 044 |  | 81 | S020NAA10CT044 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA10-AA194 | HP Steam Scrubbing Rupture Disc | Temperature | S020LFC10-BR544-500-CH3 | 500 | CH3 | HP Steam (Noise Attenuation) | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 250 | 215 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0018 | Note 7 New KKS Tag, old: S020LFC10CT044 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
62 | TH00 | S02 | 0LFC | 10 | TE | CT | 045 |  | 82 | S020NAA10CT045 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA10-AA195 | HP Steam Scrubbing Rupture Disc | Temperature | S020LFC10-BR545-500-CH3 | 500 | CH3 | HP Steam (Noise Attenuation) | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 250 | 215 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0018 | Note 7 New KKS Tag, old: S020LFC10CT045 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
63 | TH00 | S02 | 0LFC | 10 | TE | CT | 046 |  | 83 | S020NAA10CT046 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA10-AA196 | HP Steam Scrubbing Rupture Disc | Temperature | S020LFC10-BR546-500-CH3 | 500 | CH3 | HP Steam (Noise Attenuation) | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 250 | 215 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0018 | Note 7 New KKS Tag, old: S020LFC10CT046 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
74 | TH00 | S02 | 0LFC | 10 | TE | CT | 051 |  | 95 | S020NAA20CT051 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA20-AA191 | IP Steam Scrubbing Rupture Disc | Temperature | S020LFC10-BR551-500-CI3 | 500 | CI3 | IP Steam (Noise Attenuation) | Full Vac | 13.5 | -5 | 188 | - | - | °C | 0 to 250 | 188 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0020 | Note 7 New KKS Tag, old: S020LFC10CT051 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
75 | TH00 | S02 | 0LFC | 10 | TE | CT | 052 |  | 96 | S020NAA20CT052 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA20-AA192 | IP Steam Scrubbing Rupture Disc | Temperature | S020LFC10-BR552-500-CI3 | 500 | CI3 | IP Steam (Noise Attenuation) | Full Vac | 13.5 | -5 | 188 | - | - | °C | 0 to 250 | 188 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0020 | Note 7 New KKS Tag, old: S020LFC10CT052 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
76 | TH00 | S02 | 0LFC | 10 | TE | CT | 053 |  | 97 | S020NAA20CT053 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA20-AA193 | IP Steam Scrubbing Rupture Disc | Temperature | S020LFC10-BR553-500-CI3 | 500 | CI3 | IP Steam (Noise Attenuation) | Full Vac | 13.5 | -5 | 188 | - | - | °C | 0 to 250 | 188 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0020 | Note 7 New KKS Tag, old: S020LFC10CT053 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
77 | TH00 | S02 | 0LFC | 10 | TE | CT | 054 |  | 98 | S020NAA20CT054 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA20-AA194 | IP Steam Scrubbing Rupture Disc | Temperature | S020LFC10-BR554-500-CI3 | 500 | CI3 | IP Steam (Noise Attenuation) | Full Vac | 13.5 | -5 | 188 | - | - | °C | 0 to 250 | 188 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0020 | Note 7 New KKS Tag, old: S020LFC10CT054 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
85 | TH00 | S02 | 0LFC | 10 | TE | CT | 061 |  | 106 | S020NAA31CT061 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA31-AA191 | LP Steam Scrubbing A Rupture Disc | Temperature | S020LFC10-BR561-500-CL3 | 500 | CL3 | LP Steam (Noise Attenuation) | Full Vac | 5 | -5 | 143 | - | - | °C | 0 to 250 | 143 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0022 | Note 7 New KKS Tag, old: S020LFC10CT061 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
86 | TH00 | S02 | 0LFC | 10 | TE | CT | 062 |  | 107 | S020NAA31CT062 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA31-AA192 | LP Steam Scrubbing A Rupture Disc | Temperature | S020LFC10-BR562-500-CL3 | 500 | CL3 | LP Steam (Noise Attenuation) | Full Vac | 5 | -5 | 143 | - | - | °C | 0 to 250 | 143 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0022 | Note 7 New KKS Tag, old: S020LFC10CT062 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
87 | TH00 | S02 | 0LFC | 10 | TE | CT | 063 |  | 108 | S020NAA31CT063 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA31-AA193 | LP Steam Scrubbing A Rupture Disc | Temperature | S020LFC10-BR563-500-CL3 | 500 | CL3 | LP Steam (Noise Attenuation) | Full Vac | 5 | -5 | 143 | - | - | °C | 0 to 250 | 143 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0022 | Note 7 New KKS Tag, old: S020LFC10CT063 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
88 | TH00 | S02 | 0LFC | 10 | TE | CT | 064 |  | 109 | S020NAA31CT064 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA31-AA194 | LP Steam Scrubbing A Rupture Disc | Temperature | S020LFC10-BR564-500-CL3 | 500 | CL3 | LP Steam (Noise Attenuation) | Full Vac | 5 | -5 | 143 | - | - | °C | 0 to 250 | 143 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0022 | Note 7 New KKS Tag, old: S020LFC10CT064 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
89 | TH00 | S02 | 0LFC | 10 | TE | CT | 065 |  | 110 | S020NAA31CT065 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA31-AA195 | LP Steam Scrubbing A Rupture Disc | Temperature | S020LFC10-BR565-500-CL3 | 500 | CL3 | LP Steam (Noise Attenuation) | Full Vac | 5 | -5 | 143 | - | - | °C | 0 to 250 | 143 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0022 | Note 7 New KKS Tag, old: S020LFC10CT065 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
90 | TH00 | S02 | 0LFC | 10 | TE | CT | 066 |  | 111 | S020NAA31CT066 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA31-AA196 | LP Steam Scrubbing A Rupture Disc | Temperature | S020LFC10-BR566-500-CL3 | 500 | CL3 | LP Steam (Noise Attenuation) | Full Vac | 5 | -5 | 143 | - | - | °C | 0 to 250 | 143 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0022 | Note 7 New KKS Tag, old: S020LFC10CT066 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
100 | TH00 | S02 | 0LFC | 10 | TE | CT | 071 |  | 121 | S020NAA32CT071 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA32-AA191 | LP Steam Scrubbing B Rupture Disc | Temperature | S020LFC10-BR571-500-CL3 | 500 | CL3 | LP Steam (Noise Attenuation) | Full Vac | 5 | -5 | 143 | - | - | °C | 0 to 250 | 143 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0024 | Note 7 New KKS Tag, old: S020LFC10CT071 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
101 | TH00 | S02 | 0LFC | 10 | TE | CT | 072 |  | 122 | S020NAA32CT072 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA32-AA192 | LP Steam Scrubbing B Rupture Disc | Temperature | S020LFC10-BR572-500-CL3 | 500 | CL3 | LP Steam (Noise Attenuation) | Full Vac | 5 | -5 | 143 | - | - | °C | 0 to 250 | 143 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0024 | Note 7 New KKS Tag, old: S020LFC10CT072 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
102 | TH00 | S02 | 0LFC | 10 | TE | CT | 073 |  | 123 | S020NAA32CT073 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA32-AA193 | LP Steam Scrubbing B Rupture Disc | Temperature | S020LFC10-BR573-500-CL3 | 500 | CL3 | LP Steam (Noise Attenuation) | Full Vac | 5 | -5 | 143 | - | - | °C | 0 to 250 | 143 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0024 | Note 7 New KKS Tag, old: S020LFC10CT073 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
103 | TH00 | S02 | 0LFC | 10 | TE | CT | 074 |  | 124 | S020NAA32CT074 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA32-AA194 | LP Steam Scrubbing B Rupture Disc | Temperature | S020LFC10-BR574-500-CL3 | 500 | CL3 | LP Steam (Noise Attenuation) | Full Vac | 5 | -5 | 143 | - | - | °C | 0 to 250 | 143 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0024 | Note 7 New KKS Tag, old: S020LFC10CT074 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
104 | TH00 | S02 | 0LFC | 10 | TE | CT | 075 |  | 125 | S020NAA32CT075 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA32-AA195 | LP Steam Scrubbing B Rupture Disc | Temperature | S020LFC10-BR575-500-CL3 | 500 | CL3 | LP Steam (Noise Attenuation) | Full Vac | 5 | -5 | 143 | - | - | °C | 0 to 250 | 143 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0024 | Note 7 New KKS Tag, old: S020LFC10CT075 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
105 | TH00 | S02 | 0LFC | 10 | TE | CT | 076 |  | 126 | S020NAA32CT076 | Temperature Element | Separation Plant | Common Steam/Water Dump System | S020NAA32-AA196 | LP Steam Scrubbing B Rupture Disc | Temperature | S020LFC10-BR576-500-CL3 | 500 | CL3 | LP Steam (Noise Attenuation) | Full Vac | 5 | -5 | 143 | - | - | °C | 0 to 250 | 143 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0024 | Note 7 New KKS Tag, old: S020LFC10CT076 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0270SLAR1C2B1UAE065TBXW+114CM0195TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
71 | TH00 | S02 | 0NAA | 10 | FIT | CF | 010 |  | 92 | S020NAA10CF010 | Flow Transmitter (Vortex) | Separation Plant | Steam System | - | HP Steam Scrubbing | Flow | S020NAA10-BR010-1200-CH2 | 1200 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | 0 | 720 | tph | 0 to 900 | 740 | 0 to 900 | MEC-DET-1045 | CCI-DAT-1478 | PRO-PID-0019 |  | 5.6 | Custom Controls | InnovaMass | 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0‐ PGR++ | 4500191995 | 2022-12-01
66 | TH00 | S02 | 0NAA | 10 | LG | CL | 410 |  | 86 | S020NAA10CL410 | Level Gauge | Separation Plant | Steam System | S020LCE10-AA110 | HP Steam CDP | Level | S020NAA10-BR410-900-CH2 | 50 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm | - | - | 0 to 800 | MEC-DET-1230 LG Type HP08 | CCI-DAT-1471 | PRO-PID-0018 | 2"/DN50 CL300. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/36/M/S/2/1/B/N/N/X/PN/S/772MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
69 | TH00 | S02 | 0NAA | 10 | LG | CL | 450 |  | 89 | S020NAA10CL450 | Level Gauge | Separation Plant | Steam System | - | Steam Trap Bank (HP Steam Scrubbing) | Level | S020NAA10-BR450-900-CH2 | 50 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm | - | N/A | 0 to 1200 | MEC-DET-1230 LG Type HP12 | CCI-DAT-1471 | PRO-PID-0019 | 2"/DN50 CL300. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/47/M/S/2/1/B/N/N/X/PN/S/1156MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
68 | TH00 | S02 | 0NAA | 10 | LIT | DL | 451 |  | 88 | S020NAA10CL451 | Level Transmitter (GW Radar) | Separation Plant | Steam System | - | Steam Trap Bank (HP Steam Scrubbing) | Level | S020NAA10-BR450-900-CH2 | 50 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm | 0 to 1200 | N/A | 0 to 1200 | 000-MEC-DET-1231 | CCI-DAT-1469 | PRO-PID-0019 | 2"/DN50 CL300. Verify bridle nozzle dimension with vessel manufacturer. | 3.2 | Custom Controls | Rosemount | 5301HA2P1N4AM00120ABNAM1Q4Q8QTDA1S2+751AM1NAB+ | 4500191995 | 2022-11-10
[9 empty] | 90 | S020NAA10CL460 | Level Gauge | Separation Plant | Steam System | - | Steam Trap Bank (HP Steam Scrubbing) | Level | S020NAA10-BR460-900-CH2 | 50 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm | - | N/A | 0 to 800 | MEC-DET-1230 LG Type HP08 | CCI-DAT-1471 | PRO-PID-0019 | 2"/DN50 CL300. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/36/M/S/2/1/B/N/N/X/PN/S/772MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
20 | TH00 | S02 | 0NAA | 10 | PIT | DP | 021 |  | 20 | S020NAA10CP021 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA10-AT010 | HP Separator Outlet | Pressure | S020NAA10-BR010-1050-CH2 | 1050 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 17 | 0 to 23 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0012 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
21 | TH00 | S02 | 0NAA | 10 | PIT | DP | 022 |  | 21 | S020NAA10CP022 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA10-AT010 | HP Separator Outlet | Pressure | S020NAA10-BR010-1050-CH2 | 1050 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 17 | 0 to 23 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0012 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
22 | TH00 | S02 | 0NAA | 10 | PIT | DP | 023 |  | 22 | S020NAA10CP023 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA10-AT010 | HP Separator Outlet | Pressure | S020NAA10-BR010-1050-CH2 | 1050 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 17 | 0 to 23 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0012 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
| THI00 | S02 | 0NAA | 10 | TIT |  |  |  | 23 | S020NAA10CP031 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA10-AT010 | HP Separator Outlet | Pressure | S020NAA10-BR010-1050-CH2 | 1050 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 17 | 0 to 23 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0012 | SIL Note 2 | 3.7 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
| THI00 | S02 | 0NAA | 10 | TIT |  |  |  | 24 | S020NAA10CP032 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA10-AT010 | HP Separator Outlet | Pressure | S020NAA10-BR010-1050-CH2 | 1050 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 17 | 0 to 23 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0012 | SIL Note 2 | 3.7 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
| THI00 | S02 | 0NAA | 10 | TIT |  |  |  | 25 | S020NAA10CP033 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA10-AT010 | HP Separator Outlet | Pressure | S020NAA10-BR010-1050-CH2 | 1050 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 17 | 0 to 23 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0012 | SIL Note 2 | 3.7 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
70 | TH00 | S02 | 0NAA | 11 | FIT | CF | 452 |  | 91 | S020NAA11CF452 | Flow Transmitter (Orifice Flow) | Separation Plant | Steam System | - | HP Steam Scrubbing | Flow | S020NAA11-BR451-100-CH2 | 100 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | 0 | 18 | tph | TBC | 8.7 | 0 to 18 | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0019 | Note 3, Note 8 | 5.6 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P040A3SA065Q8+ | 4500191995 | 2023-02-13
81 | TH00 | S02 | 0NAA | 20 | FIT | CF | 010 |  | 102 | S020NAA20CF010 | Flow Transmitter (Vortex) | Separation Plant | Steam System | - | IP Steam Scrubbing | Flow | S020NAA20-BR010-750-CI2 | 750 | CI2 | IP Steam & Condensate | Full Vac | 13.5 | -5 | 188 | 0 | 198 | tph | 0 to 216 | 191 | 0 to 216 | MEC-DET-1045 | CCI-DAT-1478 | PRO-PID-0021 |  | 5.6 | Custom Controls | InnovaMass | 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0‐ PGR++ | 4500191995 | 2022-12-01
78 | TH00 | S02 | 0NAA | 20 | LG | CL | 410 |  | 99 | S020NAA20CL410 | Level Gauge | Separation Plant | Steam System | - | IP Steam Scrubbing Line | Level | S020NAA20-BR410-600-CI2 | 50 | CI2 | IP Steam & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | mm | - | N/A | 0 to 600 | MEC-DET-1230 LG Type IP06 | CCI-DAT-1471 | PRO-PID-0020 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/27/M/S/2/1/B/N/N/X/PN/S/559MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
80 | TH00 | S02 | 0NAA | 20 | LG | CL | 450 |  | 101 | S020NAA20CL450 | Level Gauge | Separation Plant | Steam System | - | Steam Trap Bank (IP Steam Scrubbing) | Level | S020NAA20-BR450-600-CI2 | 50 | CI2 | IP Steam & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | mm | - | N/A | 0 to 600 | MEC-DET-1230 LG Type IP06 | CCI-DAT-1471 | PRO-PID-0021 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/27/M/S/2/1/B/N/N/X/PN/S/559MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
82 | TH00 | S02 | 0NAA | 20 | LG | CL | 460 |  | 103 | S020NAA20CL460 | Level Gauge | Separation Plant | Steam System | - | Steam Trap Bank (IP Steam Scrubbing) | Level | S020NAA20-BR460-600-CI2 | 50 | CI2 | IP Steam & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | mm | - | N/A | 0 to 600 | MEC-DET-1230 LG Type IP06 | CCI-DAT-1471 | PRO-PID-0021 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/27/M/S/2/1/B/N/N/X/PN/S/559MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
33 | TH00 | S02 | 0NAA | 20 | PIT | DP | 021 |  | 40 | S020NAA20CP021 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA20-AT010 | IP Separator Outlet | Pressure | S020NAA20-BR010-750-CI2 | 750 | CI2 | IP Steam & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | bar(g) | -1 to 55 | 9 | 0 to 15 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0020 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
34 | TH00 | S02 | 0NAA | 20 | PIT | DP | 022 |  | 41 | S020NAA20CP022 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA20-AT010 | IP Separator Outlet | Pressure | S020NAA20-BR010-750-CI2 | 750 | CI2 | IP Steam & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | bar(g) | -1 to 55 | 9 | 0 to 15 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0020 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
35 | TH00 | S02 | 0NAA | 20 | PIT | DP | 023 |  | 42 | S020NAA20CP023 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA20-AT010 | IP Separator Outlet | Pressure | S020NAA20-BR010-750-CI2 | 750 | CI2 | IP Steam & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | bar(g) | -1 to 55 | 9 | 0 to 15 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0020 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
| TH00 | S02 | 0NAA | 20 | PIT |  |  |  | 43 | S020NAA20CP031 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA20-AT010 | IP Separator Outlet | Pressure | S020NAA20-BR010-750-CI2 | 750 | CI2 | IP Steam & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | bar(g) | -1 to 55 | 9 | 0 to 13 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0020 | SIL Note 2 | 3.7 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
| TH00 | S02 | 0NAA | 20 | PIT |  |  |  | 44 | S020NAA20CP032 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA20-AT010 | IP Separator Outlet | Pressure | S020NAA20-BR010-750-CI2 | 750 | CI2 | IP Steam & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | bar(g) | -1 to 55 | 9 | 0 to 13 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0020 | SIL Note 2 | 3.7 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
| TH00 | S02 | 0NAA | 20 | PIT |  |  |  | 45 | S020NAA20CP033 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA20-AT010 | IP Separator Outlet | Pressure | S020NAA20-BR010-750-CI2 | 750 | CI2 | IP Steam & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | bar(g) | -1 to 55 | 9 | 0 to 13 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0020 | SIL Note 2 | 3.7 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
95 | TH00 | S02 | 0NAA | 31 | FIT | CF | 010 |  | 116 | S020NAA31CF010 | Flow Transmitter (Vortex) | Separation Plant | Steam System | - | LP Steam Scrubbing A | Flow | S020NAA31-BR010-1300-CL2 | 1300 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | 0 | 180 | tph | 0 to 216 | 162 | 0 to 216 | MEC-DET-1045 | CCI-DAT-1478 | PRO-PID-0023 |  | 5.6 | Custom Controls | InnovaMass | 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0‐ PGR++ | 4500191995 | 2022-12-01
92 | TH00 | S02 | 0NAA | 31 | LG | CL | 410 |  | 113 | S020NAA31CL410 | Level Gauge | Separation Plant | Steam System | - | LP Steam Scrubbing A Line | Level | S020NAA31-BR410-1050-CL2 | 50 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | mm | - | N/A | 0 to 1000 | MEC-DET-1230 LG Type LP10 | CCI-DAT-1471 | PRO-PID-0022 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
94 | TH00 | S02 | 0NAA | 31 | LG | CL | 450 |  | 115 | S020NAA31CL450 | Level Gauge | Separation Plant | Steam System | - | Steam Trap Bank (LP Steam Scrubbing A) | Level | S020NAA31-BR450-1050-CL2 | 50 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | mm | - | N/A | 0 to 1000 | MEC-DET-1230 LG Type LP10 | CCI-DAT-1471 | PRO-PID-0023 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
96 | TH00 | S02 | 0NAA | 31 | LG | CL | 460 |  | 117 | S020NAA31CL460 | Level Gauge | Separation Plant | Steam System | - | Steam Trap Bank (LP Steam Scrubbing A) | Level | S020NAA31-BR460-1050-CL2 | 50 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | mm | - | N/A | 0 to 1000 | MEC-DET-1230 LG Type LP10 | CCI-DAT-1471 | PRO-PID-0023 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
55 | TH00 | S02 | 0NAA | 31 | PIT | DP | 021 |  | 72 | S020NAA31CP021 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA30-AT010 | LP Separator A Outlet | Pressure | S020NAA31-BR010-1050-CL2 | 1050 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 |  | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
56 | TH00 | S02 | 0NAA | 31 | PIT | DP | 022 |  | 73 | S020NAA31CP022 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA30-AT010 | LP Separator A Outlet | Pressure | S020NAA31-BR010-1050-CL2 | 1050 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 |  | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
57 | TH00 | S02 | 0NAA | 31 | PIT | DP | 023 |  | 74 | S020NAA31CP023 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA30-AT010 | LP Separator A Outlet | Pressure | S020NAA31-BR010-1050-CL2 | 1050 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 |  | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
| THI00 | S02 | 0NAA | 31 | PIT |  |  |  | 75 | S020NAA31CP031 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA30-AT010 | LP Separator A Outlet | Pressure | S020NAA31-BR010-1050-CL2 | 1050 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 | SIL Note 2 | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
| THI00 | S02 | 0NAA | 31 | PIT |  |  |  | 76 | S020NAA31CP032 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA30-AT010 | LP Separator A Outlet | Pressure | S020NAA31-BR010-1050-CL2 | 1050 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 | SIL Note 2 | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
| THI00 | S02 | 0NAA | 31 | PIT |  |  |  | 77 | S020NAA31CP033 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA30-AT010 | LP Separator A Outlet | Pressure | S020NAA31-BR010-1050-CL2 | 1050 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 | SIL Note 2 | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
109 | TH00 | S02 | 0NAA | 32 | FIT | CF | 010 |  | 130 | S020NAA32CF010 | Flow Transmitter (Vortex) | Separation Plant | Steam System | - | LP Steam Scrubbing B | Flow | S020NAA32-BR010-1300-CL2 | 1300 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | 0 | 180 | tph | 0 to 216 | 162 | 0 to 216 | MEC-DET-1045 | CCI-DAT-1478 | PRO-PID-0025 |  | 5.6 | Custom Controls | InnovaMass | 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0‐ PGR++ | 4500191995 | 2022-12-01
106 | TH00 | S02 | 0NAA | 32 | LG | CL | 410 |  | 127 | S020NAA32CL410 | Level Gauge | Separation Plant | Steam System | - | LP Steam Scrubbing B Line | Level | S020NAA32-BR410-1050-CL2 | 50 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | mm | - | N/A | 0 to 1000 | MEC-DET-1230 LG Type LP10 | CCI-DAT-1471 | PRO-PID-0024 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
108 | TH00 | S02 | 0NAA | 32 | LG | CL | 450 |  | 129 | S020NAA32CL450 | Level Gauge | Separation Plant | Steam System | - | Steam Trap Bank (LP Steam Scrubbing B) | Level | S020NAA32-BR450-1050-CL2 | 50 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | mm | - | N/A | 0 to 1000 | MEC-DET-1230 LG Type LP10 | CCI-DAT-1471 | PRO-PID-0025 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
110 | TH00 | S02 | 0NAA | 32 | LG | CL | 460 |  | 131 | S020NAA32CL460 | Level Gauge | Separation Plant | Steam System | - | Steam Trap Bank (LP Steam Scrubbing B) | Level | S020NAA32-BR460-1050-CL2 | 50 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | mm | - | N/A | 0 to 1000 | MEC-DET-1230 LG Type LP10 | CCI-DAT-1471 | PRO-PID-0025 | 2"/DN50 CL150. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/38/M/S/2/1/B/N/N/X/PN/S/981MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
52 | TH00 | S02 | 0NAA | 32 | PIT | DP | 021 |  | 66 | S020NAA32CP021 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA30-AT020 | LP Separator B Outlet | Pressure | S020NAA32-BR010-1050-CL2 | 1050 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 |  | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
53 | TH00 | S02 | 0NAA | 32 | PIT | DP | 022 |  | 67 | S020NAA32CP022 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA30-AT020 | LP Separator B Outlet | Pressure | S020NAA32-BR010-1050-CL2 | 1050 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 |  | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
54 | TH00 | S02 | 0NAA | 32 | PIT | DP | 023 |  | 68 | S020NAA32CP023 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA30-AT020 | LP Separator B Outlet | Pressure | S020NAA32-BR010-1050-CL2 | 1050 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 |  | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
| TH00 | S02 | 0NAA | 32 | PIT |  |  |  | 69 | S020NAA32CP031 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA30-AT020 | LP Separator B Outlet | Pressure | S020NAA32-BR010-1050-CL2 | 1050 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 | SIL Note 2 | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
| TH00 | S02 | 0NAA | 32 | PIT |  |  |  | 70 | S020NAA32CP032 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA30-AT020 | LP Separator B Outlet | Pressure | S020NAA32-BR010-1050-CL2 | 1050 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 | SIL Note 2 | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
| TH00 | S02 | 0NAA | 32 | PIT |  |  |  | 71 | S020NAA32CP033 | Pressure Indicating Transmitter | Separation Plant | Steam System | S020NDA30-AT020 | LP Separator B Outlet | Pressure | S020NAA32-BR010-1050-CL2 | 1050 | CL2 | LP Steam & Condensate | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 | SIL Note 2 | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8QT c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
23 | TH00 | S02 | 0NDA | 10 | LIT | DL | 011 |  | 26 | S020NDA10CL011 | Level Transmitter (GW Radar) | Separation Plant | Production Piping System | S020NDA10-BB010 | HP SGW Drum | Level | S020NDA10-BR311-80-CH4 | 80 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | NDA-MEC-DET-1052 | CCI-DAT-1469 | PRO-PID-0012 | Verify bridle nozzle dimension with vessel manufacturer. 3"/DN80 CL300. SIL Note 2. | 3.2 | Custom Controls | Rosemount | 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3+751AM1NAB+ | 4500191995 | 2022-11-10
24 | TH00 | S02 | 0NDA | 10 | LIT | DL | 012 |  | 27 | S020NDA10CL012 | Level Transmitter (GW Radar) | Separation Plant | Production Piping System | S020NDA10-BB010 | HP SGW Drum | Level | S020NDA10-BR312-80-CH4 | 80 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | NDA-MEC-DET-1052 | CCI-DAT-1469 | PRO-PID-0012 | Verify bridle nozzle dimension with vessel manufacturer. 3"/DN80 CL300. SIL Note 2. | 3.2 | Custom Controls | Rosemount | 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3+751AM1NAB+ | 4500191995 | 2022-11-10
25 | TH00 | S02 | 0NDA | 10 | LIT | DL | 013 |  | 28 | S020NDA10CL013 | Level Transmitter (GW Radar) | Separation Plant | Production Piping System | S020NDA10-BB010 | HP SGW Drum | Level | S020NDA10-BR313-80-CH4 | 80 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | NDA-MEC-DET-1052 | CCI-DAT-1469 | PRO-PID-0012 | Verify bridle nozzle dimension with vessel manufacturer. 3"/DN80 CL300. SIL Note 2. | 3.2 | Custom Controls | Rosemount | 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3+751AM1NAB+ | 4500191995 | 2022-11-10
| TH00 | S02 | 0NDA | 10 | LIT |  |  |  | 29 | S020NDA10CL014 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA10-BB010 | HP SGW Drum Loop Seal | Level | S020NDA10-BR313-80-CH4 | 80 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm | 0 to 5690 | - | 0 to 5690 | CCI-DET-2704 MEC-SCN-3036 | CCI-DAT-1467 | PRO-PID-0012 | Replaced 3"/DN80 CL 300, SIL Note 2 | 7 | Custom Controls | Rosemount | 3051S2CD3A2B12A1BM5Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC61AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
26 | TH00 | S02 | 0NDA | 10 | LIT | DL | 021 |  | 30 | S020NDA10CL021 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA10-BB010 | HP SGW Drum | Level | S020NDA10-BR333-80-CH4 | 80 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | CCI-DET-2704 NDA-MEC-DET-1050 | CCI-DAT-1467 | PRO-PID-0012 | Replaced 3"/DN80 CL 300 | 7 | Custom Controls | Rosemount | 3051S2CD2A2B12A1BM5Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC58AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
27 | TH00 | S02 | 0NDA | 10 | LIT | DL | 022 |  | 31 | S020NDA10CL022 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA10-BB010 | HP SGW Drum | Level | S020NDA10-BR332-80-CH4 | 80 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | CCI-DET-2704 NDA-MEC-DET-1050 | CCI-DAT-1467 | PRO-PID-0012 | Replaced 3"/DN80 CL 300 | 7 | Custom Controls | Rosemount | 3051S2CD2A2B12A1BM5Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC58AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
28 | TH00 | S02 | 0NDA | 10 | LIT | DL | 023 |  | 32 | S020NDA10CL023 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA10-BB010 | HP SGW Drum | Level | S020NDA10-BR331-80-CH4 | 80 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | CCI-DET-2704 NDA-MEC-DET-1050 | CCI-DAT-1467 | PRO-PID-0012 | Replaced 3"/DN80 CL 300 | 7 | Custom Controls | Rosemount | 3051S2CD2A2B12A1BM5Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC58AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
29 | TH00 | S02 | 0NDA | 10 | LG | CL | 031 |  | 33 | S020NDA10CL031 | Level Gauge | Separation Plant | Production Piping System | S020NDA10-BB010 | HP SGW Drum | Level | S020NDA10-BR331-80-CH4 | 80 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm | - | 1676 | 335 to 3018 | CCI-DET-2705 NDA-MEC-DET-1050 | CCI-DAT-1471 | PRO-PID-0012 | 2"/DN50 CL300. Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/88/M/S/2/1/B/N/N/X/PN/S/2560MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
19 | TH00 | S02 | 0NDA | 10 | PIT | CP | 010 |  | 19 | S020NDA10CP010 | Pressure Indicating Transmitter | Separation Plant | Production Piping System | S020NDA10-AT010 | HP Separator Inlet | Pressure | S020NDA10-BR013-1050-CH2 | 1050 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 17 | 0 to 23 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0012 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
18 | TH00 | S02 | 0NDA | 10 | TIT | CT | 010 |  | 18 | S020NDA10CT010 | Temperature Indicating Transmitter | Separation Plant | Production Piping System | L050NDA10-AA030 | TH12 Two Phase Isolation Valve Outlet | Temperature | S020NDA10-BR011-750-CH2 | 750 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 250 | 217.9 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1465 | PRO-PID-0011 | Note 7 | 4.8 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0350SLAR1C2B1UAE065TBXW+114CM0275TAC2SC075AQ5Q8R21XW | 4500191995 | 2023-01-09
12 | TH00 | S02 | 0NDA | 10 | TIT | CT | 020 |  | 12 | S020NDA10CT020 | Temperature Indicating Transmitter | Separation Plant | Production Piping System | L060NDA10-AA030 | TH28 Two Phase Isolation Valve Outlet | Temperature | S020NDA10-BR012-800-CH2 | 800 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 250 | 217.9 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1465 | PRO-PID-0011 | Note 7 | 4.8 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0370SLAR1C2B1UAE065TBXW+114CM0295TAC2SC075AQ5Q8R21XW | 4500191995 | 2023-01-09
6 | TH00 | S02 | 0NDA | 10 | TIT | CT | 030 |  | 6 | S020NDA10CT030 | Temperature Indicating Transmitter | Separation Plant | Production Piping System | L070NDA10-AA030 | TH26 Two Phase Isolation Valve Outlet | Temperature | S020NDA10-BR013-1050-CH2 | 800 | CH2 | HP, Two Phase Steam & Condensate | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 250 | 217.9 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1465 | PRO-PID-0011 | Note 7 | 4.8 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0370SLAR1C2B1UAE065TBXW+114CM0295TAC2SC075AQ5Q8R21XW | 4500191995 | 2023-01-09
30 | TH00 | S02 | 0NDA | 20 | FIT | DF | 010 |  | 34 | S020NDA20CF010 | Flow Transmitter (Orifice Flow) | Separation Plant | Production Piping System | S020NDA10-BB010 | HP SGW Drum Outlet | Flow | S020NDA20-BR010-900-CH4 | 900 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | 0 | 3222 | tph | 0 to 3222 | 2530 | 0 to 3222 | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0012 | Note 3, Note 8 | 6.3 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P999A3SD065Q8C0064+ | 4500191995 | 2023-04-19
31 | TH00 | S02 | 0NDA | 20 | FIT | DF | 020 |  | 35 | S020NDA20CF020 | Flow Transmitter (Orifice Flow) | Separation Plant | Production Piping System | S020NDA10-BB010 | HP SGW Drum Outlet | Flow | S020NDA20-BR010-900-CH4 | 900 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | 0 | 3222 | tph | 0 to 3222 | 2916 | 0 to 3222 | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0012 | CEL to SPECIFY Note 3, Note 8 | 6.3 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P999A3SD065Q8C0064+ | 4500191995 | 2023-04-19
36 | TH00 | S02 | 0NDA | 20 | LIT | DL | 011 |  | 46 | S020NDA20CL011 | Level Transmitter (GW Radar) | Separation Plant | Production Piping System | S020NDA20-BB010 | IP SGW Drum | Level | S020NDA20-BR311-80-CI4 | 80 | CI4 | IP SGW & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | NDA-MEC-DET-1055 | CCI-DAT-1469 | PRO-PID-0013 | Verify bridle nozzle dimension with vessel manufacturer. 3"/DN80 CL150. SIL Note 2. | 3.2 | Custom Controls | Rosemount | 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3+751AM1NAB+ | 4500191995 | 2022-11-10
37 | TH00 | S02 | 0NDA | 20 | LIT | DL | 012 |  | 47 | S020NDA20CL012 | Level Transmitter (GW Radar) | Separation Plant | Production Piping System | S020NDA20-BB010 | IP SGW Drum | Level | S020NDA20-BR312-80-CI4 | 80 | CI4 | IP SGW & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | NDA-MEC-DET-1055 | CCI-DAT-1469 | PRO-PID-0013 | Verify bridle nozzle dimension with vessel manufacturer. 3"/DN80 CL150. SIL Note 2. | 3.2 | Custom Controls | Rosemount | 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3+751AM1NAB+ | 4500191995 | 2022-11-10
38 | TH00 | S02 | 0NDA | 20 | LIT | DL | 013 |  | 48 | S020NDA20CL013 | Level Transmitter (GW Radar) | Separation Plant | Production Piping System | S020NDA20-BB010 | IP SGW Drum | Level | S020NDA20-BR313-80-CI4 | 80 | CI4 | IP SGW & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | NDA-MEC-DET-1055 | CCI-DAT-1469 | PRO-PID-0013 | Verify bridle nozzle dimension with vessel manufacturer. 3"/DN80 CL150. SIL Note 2. | 3.2 | Custom Controls | Rosemount | 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3+751AM1NAB+ | 4500191995 | 2022-11-10
| TH00 | S02 | 0NDA | 20 | LIT |  |  |  | 49 | S020NDA20CL014 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA20-BB010 | IP SGW Drum loop Seal | Level | S020NDA20-BR313-80-CI4 | 80 | CI4 | IP SGW & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | mm | 0 to 5440 | - | 0 to 5440 | CCI-DET-2704 MEC-SCN-3038 | CCI-DAT-1467 | PRO-PID-0013 | Replaced 3"/DN80 CL 300, SIL Note 2 | 7 | Custom Controls | Rosemount | 3051S2CD3A2B12A1BM5Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC61AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
39 | TH00 | S02 | 0NDA | 20 | LIT | DL | 021 |  | 50 | S020NDA20CL021 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA20-BB010 | IP SGW Drum | Level | S020NDA20-BR333-80-CI4 | 80 | CI4 | IP SGW & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | CCI-DET-2704 NDA-MEC-DET-1053 | CCI-DAT-1467 | PRO-PID-0013 | Replaced 3"/DN80 CL 150 | 7 | Custom Controls | Rosemount | 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
40 | TH00 | S02 | 0NDA | 20 | LIT | DL | 022 |  | 51 | S020NDA20CL022 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA20-BB010 | IP SGW Drum | Level | S020NDA20-BR332-80-CI4 | 80 | CI4 | IP SGW & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | CCI-DET-2704 NDA-MEC-DET-1053 | CCI-DAT-1467 | PRO-PID-0013 | Replaced 3"/DN80 CL 150 | 7 | Custom Controls | Rosemount | 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
41 | TH00 | S02 | 0NDA | 20 | LIT | DL | 023 |  | 52 | S020NDA20CL023 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA20-BB010 | IP SGW Drum | Level | S020NDA20-BR331-80-CI4 | 80 | CI4 | IP SGW & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | CCI-DET-2704 NDA-MEC-DET-1053 | CCI-DAT-1467 | PRO-PID-0013 | Replaced 3"/DN80 CL 150 | 7 | Custom Controls | Rosemount | 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
42 | TH00 | S02 | 0NDA | 20 | LG | CL | 031 |  | 53 | S020NDA20CL031 | Level Gauge | Separation Plant | Production Piping System | S020NDA20-BB010 | IP SGW Drum | Level | S020NDA20-BR331-80-CI4 | 80 | CI4 | IP SGW & Condensate | Full Vac | 13.5 | -5 | 188 | - | - | mm | - | 1676 | 335 to 3018 | CCI-DET-2705 NDA-MEC-DET-1053 | CCI-DAT-1471 | PRO-PID-0013 | 2"/DN50 CL150 Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/88/M/S/2/1/B/N/N/X/PN/S/2560MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
32 | TH00 | S02 | 0NDA | 20 | PIT | CP | 010 |  | 39 | S020NDA20CP010 | Pressure Indicating Transmitter | Separation Plant | Production Piping System | S020NDA20-AT010 | IP Separator Inlet | Pressure | S020NDA20-BR021-750-CI1 | 750 | CI1 | IP Two Phase | Full Vac | 13.5 | -5 | 188 | - | - | bar(g) | -1 to 55 | 9 | 0 to 15 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0013 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
| TH00 | S02 | 0NDA | 20 | RT | CR | 020 |  | 36 | S020NDA20CR001 | Corrosometer | Separation Plant | Production Piping System | - | HP SGW Drum Outlet | Corrosion | S020NDA20-BR010-900-CH4 | 900 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm/Time Unit | * | * | TBC | TBC | COSASCO Model 3500/3500HT ER-420 | PRO-PID-0012 | 1"NPT CEL Specified SIL Note 2 | 5.6 | Cosasco | Cosasco | 3520-T10-K03005+ER-420+CI-RS-G10180 | 4500189863 | 2022-11-10
| TH00 | S02 | 0NDA | 20 | RT | CR | 020 |  | 37 | S020NDA20CR002 | Corrosometer | Separation Plant | Production Piping System | - | HP SGW Drum Outlet | Corrosion | S020NDA20-BR010-900-CH4 | 900 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm/Time Unit | * | * | TBC | TBC | COSASCO Model 3500/3500HT ER-420 | PRO-PID-0012 | 1"NPT CEL Specified SIL Note 2 | 5.6 | Cosasco | Cosasco | 3520-T10-K03005+ER-420+CI-RS-G10180 | 4500189863 | 2022-11-10
| TH00 | S02 | 0NDA | 20 | RT | CR | 020 |  | 38 | S020NDA20CR003 | Corrosometer | Separation Plant | Production Piping System | - | HP SGW Drum Outlet | Corrosion | S020NDA20-BR010-900-CH4 | 900 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | mm/Time Unit | * | * | TBC | TBC | COSASCO Model 3500/3500HT ER-420 | PRO-PID-0012 | 1"NPT CEL Specified SIL Note 2 | 5.6 | Cosasco | Cosasco | 3520-T10-K03005+ER-420+CI-RS-G10180 | 4500189863 | 2022-11-10
43 | TH00 | S02 | 0NDA | 30 | RT | CR | 011 |  | 54 | S020NDA30CR004 | Corrosometer | Separation Plant | Production Piping System | - | IP SGW Drum Outlet | Corrosion | S020NDA30-BR010-900-CL4 | 900 | CL4 | LP Two Phase | Full Vac | 5 | -5 | 143 | - | - | mm/Time Unit | * | * | TBC | 1" NPT | COSASCO Model 3500/3500HT ER-420 | PRO-PID-0013 | CEL Specified SIL Note 2 New KKS Tag, old: S020NDA20CR004 | 6.5 | Cosasco | Cosasco | 3520-T10-K03005+ER-420+CI-RS-G10180 | 4500189863 | 2022-11-10
210 | TH00 | S02 | 0NDA | 21 | FIT | DF | 010 |  | 145 | S020NDA21CF010 | Flow Transmitter (Orifice Flow) | Separation Plant | Production Piping System | S020NDA21-AP010 | Acid Dilution SGW Pump A Outlet | Flow | S020NDA21-BR021-80-CH4 | 80 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | 0 | 495 | l/m | 0 to 495 | 450 | 0 to 495 | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0030 | Note 3, Note 8 | 5.6 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P030A3SA065Q8+ | 4500191995 | 2023-02-13
| TH00 | S02 | 0NDA | 21 | PIT |  |  |  | 143 | S020NDA21CP010 | Pressure Indicating Transmitter | Separation Plant | Production Piping System | S020NDA21-AP010 | Acid Dilution SGW Pump A Intlet | Pressure | S020NDA21-BR011-100-CH4 | 100 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 17 | 0 to 25 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0030 |  | 5.6 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
209 | TH00 | S02 | 0NDA | 21 | PIT | CP | 510 |  | 144 | S020NDA21CP011 | Pressure Indicating Transmitter | Separation Plant | Production Piping System | S020NDA21-AP010 | Acid Dilution SGW Pump A Outlet | Pressure | S020NDA21-BR021-80-CH4 | 80 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 18.8 | 0 to 25 | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0030 |  | 6.2 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
208 | TH00 | S02 | 0NDA | 21 | TE | CT | 010 |  | 142 | S020NDA21CT010 | Temperature Element | Separation Plant | Production Piping System | S020NDA21-AP010 | Acid Dilution SGW Pump A Intlet | Temperature | S020NDA21-BR011-100-CH4 | 100 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 250 | 202 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0030 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0155SLAR1C2B1UAE065TBXW+114CM0080TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
214 | TH00 | S02 | 0NDA | 22 | FIT | DF | 020 |  | 150 | S020NDA22CF020 | Flow Transmitter (Orifice Flow) | Separation Plant | Production Piping System | S020NDA22-AP020 | Acid Dilution SGW Pump B Outlet | Flow | S020NDA22-BR022-80-CH4 | 80 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | 0 | 495 | l/m | 0 to 495 | 450 | 0 to 495 | CCI-DET-2702 | CCI-DAT-1472 PRO-CAL-0039 | PRO-PID-0030 | Note 3, Note 8 | 5.6 | Custom Controls | Rosemount | 3051S1CD2A2A11A1BM5P1Q4Q8T1 c/w 0305RC52B11B4L4+1595P030A3SA065Q8+ | 4500191995 | 2023-02-13
| TH00 | S02 | 0NDA | 22 | PIT |  |  |  | 148 | S020NDA22CP020 | Pressure Indicating Transmitter | Separation Plant | Production Piping System | S020NDA22-AP020 | Acid Dilution SGW Pump B Intlet | Pressure | S020NDA22-BR012-100-CH4 | 100 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 17 | 0 to 25 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0030 |  | 5.6 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
213 | TH00 | S02 | 0NDA | 22 | PIT | CP | 520 |  | 149 | S020NDA22CP021 | Pressure Indicating Transmitter | Separation Plant | Production Piping System | S020NDA22-AP020 | Acid Dilution SGW Pump B Outlet | Pressure | S020NDA22-BR022-80-CH4 | 80 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | bar(g) | -1 to 55 | 18.8 | 0 to 25 | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0030 |  | 6.2 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
212 | TH00 | S02 | 0NDA | 22 | TE | CT | 020 |  | 147 | S020NDA22CT020 | Temperature Element | Separation Plant | Production Piping System | S020NDA22-AP020 | Acid Dilution SGW Pump B Intlet | Temperature | S020NDA22-BR012-100-CH4 | 100 | CH4 | HP SGW & Condensate | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 250 | 202 | 0 to 250 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0030 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0155SLAR1C2B1UAE065TBXW+114CM0080TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
424 | TH00 | S02 | 0NDA | 23 | FIT | CF | 011 |  | 200 | S020NDA23CF011 | Flow Transmitter (Magnetic) | Separation Plant | Production Piping System | - | HP SGW pH Monitoring Skid | Flow | S020NDA23-BR602-15-S10 | 15 | S10 | TP SGW (Acidified) | Full Vac | 23 | -5 | 215 | 0 | Refer to Specification | l/m | Refer to Specification | Refer to Specification | 0 to 10 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0101 | Note 1 | 5.6 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | 4500192700 | 2022-11-10
419 | TH00 | S02 | 0NDA | 23 | PDIT | CP | 511 |  | 195 | S020NDA23CP511 | Pressure Differential Transmitter | Separation Plant | Production Piping System | - | HP SGW pH Monitoring Skid | Pressure | S020NDA23-BR602-15-S10 | 15 | S10 | TP SGW (Acidified) | Full Vac | 23 | -5 | 215 | - | - | bar(g) | 0 to 20 | 0.23 | 0 to 20 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0101 | Note 1 | 5.6 | Custom Controls | Rosemount | 3051CD3A02A1BS5M4Q4Q8T1Q15+0305RC52B11B4L4SG | 4500192700 | 2023-01-13
421 | TH00 | S02 | 0NDA | 23 | PI | CP | 512 |  | 197 | S020NDA23CP512 | Pressure Gauge | Separation Plant | Production Piping System | - | HP SGW pH Monitoring Skid | Pressure | S020NDA23-BR602-15-S10 | 15 | S10 | TP SGW (Acidified) | Full Vac | 23 | -5 | 215 | - | - | bar(g) | 0 to 25 | 8 | - | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0101 | Note 1 | 7.5 | Wika | Wika | 72039878+14503369+0731277 | 4500198881 | 2023-04-20
423 | TH00 | S02 | 0NDA | 23 | AT | CQ | 010 |  | 199 | S020NDA23CQ010 | Analyser Transmitter (pH) | Separation Plant | Production Piping System | - | HP SGW pH Monitoring Skid | pH | S020NDA23-BR602-15-S10 | 15 | S10 | TP SGW (Acidified) | Full Vac | 23 | -5 | 215 | - | - | pH | 0 to 14 | 5 | 3.5 to 8.5 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0101 | Note 1 |  | EMC | E+H | CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 + CPA-C111 + Cover | 4500191501 | 2022-11-10
422 | TH00 | S02 | 0NDA | 23 | TIT | CT | 011 |  | 198 | S020NDA23CT011 | Temperature Indicating Transmitter | Separation Plant | Production Piping System | - | HP SGW pH Monitoring Skid | Temperature | S020NDA23-BR602-15-S10 | 15 | S10 | TP SGW (Acidified) | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 215 | 60 | 0 to 100 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0101 | Note 1, Note 7 | 4.6 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8R21XW | 4500192700 | 2023-01-12
430 | TH00 | S02 | 0NDA | 24 | FIT | CF | 020 |  | 206 | S020NDA24CF020 | Flow Transmitter (Magnetic) | Separation Plant | Production Piping System | - | HP SGW pH Monitoring Skid | Flow | S020NDA24-BR603-15-S10 | 15 | S10 | TP SGW (Acidified) | Full Vac | 23 | -5 | 215 | 0 | Refer to Specification | l/m | Refer to Specification | Refer to Specification | 0 to 10 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0101 | Note 1 | 5.6 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | 4500192700 | 2022-11-10
425 | TH00 | S02 | 0NDA | 24 | PDIT | CP | 521 |  | 201 | S020NDA24CP521 | Pressure Differential Transmitter | Separation Plant | Production Piping System | - | HP SGW pH Monitoring Skid | Pressure | S020NDA24-BR603-15-S10 | 15 | S10 | TP SGW (Acidified) | Full Vac | 23 | -5 | 215 | - | - | bar(g) | 0 to 20 | 0.23 | 0 to 20 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0101 | Note 1 | 5.6 | Custom Controls | Rosemount | 3051CD3A02A1BS5M4Q4Q8T1Q15+0305RC52B11B4L4SG | 4500192700 | 2023-01-13
427 | TH00 | S02 | 0NDA | 24 | PI | CP | 522 |  | 203 | S020NDA24CP522 | Pressure Gauge | Separation Plant | Production Piping System | - | HP SGW pH Monitoring Skid | Pressure | S020NDA24-BR603-15-S10 | 15 | S10 | TP SGW (Acidified) | Full Vac | 23 | -5 | 215 | - | - | bar(g) | 0 to 25 | 8 | - | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0101 | Note 1 | 7.5 | Wika | Wika | 72039878+14503369+0731277 | 4500198881 | 2023-04-20
429 | TH00 | S02 | 0NDA | 24 | AT | CQ | 020 |  | 205 | S020NDA24CQ020 | Analyser Transmitter (pH) | Separation Plant | Production Piping System | - | HP SGW pH Monitoring Skid | pH | S020NDA24-BR603-15-S10 | 15 | S10 | TP SGW (Acidified) | Full Vac | 23 | -5 | 215 | - | - | pH | 0 to 14 | 5 | 3.5 to 8.5 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0101 | Note 1 |  | EMC | E+H | CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 + CPA-C111 + Cover | 4500191501 | 2022-11-10
428 | TH00 | S02 | 0NDA | 24 | TIT | CT | 021 |  | 204 | S020NDA24CT021 | Temperature Indicating Transmitter | Separation Plant | Production Piping System | - | HP SGW pH Monitoring Skid | Temperature | S020NDA24-BR603-15-S10 | 15 | S10 | TP SGW (Acidified) | Full Vac | 23 | -5 | 215 | - | - | °C | 0 to 215 | 60 | 0 to 100 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0101 | Note 1, Note 7 | 4.6 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8R21XW | 4500192700 | 2023-01-12
45 | TH00 | S02 | 0NDA | 30 | LIT | DL | 011 |  | 57 | S020NDA30CL011 | Level Transmitter (GW Radar) | Separation Plant | Production Piping System | S020NDA30-BB010 | LP SGW Drum | Level | S020NDA30-BR311-80-CL4 | 80 | CL4 | LP SGW & Condensate | Full Vac | 6.5 | -5 | 143 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | NDA-MEC-DET-1055 | CCI-DAT-1469 | PRO-PID-0014 | Verify bridle nozzle dimension with vessel manufacturer. 3"/DN80 CL150. SIL Note 2. | 3.2 | Custom Controls | Rosemount | 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3+751AM1NAB+ | 4500191995 | 2022-11-10
46 | TH00 | S02 | 0NDA | 30 | LIT | DL | 012 |  | 58 | S020NDA30CL012 | Level Transmitter (GW Radar) | Separation Plant | Production Piping System | S020NDA30-BB010 | LP SGW Drum | Level | S020NDA30-BR312-80-CL4 | 80 | CL4 | LP SGW & Condensate | Full Vac | 6.5 | -5 | 143 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | NDA-MEC-DET-1055 | CCI-DAT-1469 | PRO-PID-0014 | Verify bridle nozzle dimension with vessel manufacturer. 3"/DN80 CL150. SIL Note 2. | 3.2 | Custom Controls | Rosemount | 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3+751AM1NAB+ | 4500191995 | 2022-11-10
47 | TH00 | S02 | 0NDA | 30 | LIT | DL | 013 |  | 59 | S020NDA30CL013 | Level Transmitter (GW Radar) | Separation Plant | Production Piping System | S020NDA30-BB010 | LP SGW Drum | Level | S020NDA30-BR313-80-CL4 | 80 | CL4 | LP SGW & Condensate | Full Vac | 6.5 | -5 | 143 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | NDA-MEC-DET-1055 | CCI-DAT-1469 | PRO-PID-0014 | Verify bridle nozzle dimension with vessel manufacturer. 3"/DN80 CL150. SIL Note 2. | 3.2 | Custom Controls | Rosemount | 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3+751AM1NAB+ | 4500191995 | 2022-11-10
| TH00 | S02 | 0NDA | 30 | LIT |  |  |  | 60 | S020NDA30CL014 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA30-BB010 | LP SGW Drum loop Seal | Level | S020NDA30-BR313-80-CL4 | 80 | CL4 | LP SGW & Condensate | Full Vac | 6.5 | -5 | 143 | - | - | mm | 0 to 5640 | - | 0 to 5640 | CCI-DET-2704 MEC-SCN-3039 | CCI-DAT-1467 | PRO-PID-0014 | Replaced 3"/DN80 CL 300, SIL Note 2 | 7 | Custom Controls | Rosemount | 3051S2CD3A2B12A1BM5Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC61AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
| TH00 | S02 | 0NDA | 30 | LIT |  |  |  | 61 | S020NDA30CL015 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA30-BB010 | LP SGW Drum loop Seal | Level | S020NDA30-BR313-80-CL4 | 80 | CL4 | LP SGW & Condensate | Full Vac | 6.5 | -5 | 143 | - | - | mm | 0 to 5640 | - | 0 to 5640 | CCI-DET-2704 | CCI-DAT-1467 | PRO-PID-0014 | Replaced 3"/DN80 CL 300, SIL Note 2 | 7 | Custom Controls | Rosemount | 3051S2CD3A2B12A1BM5Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC61AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
48 | TH00 | S02 | 0NDA | 30 | LIT | DL | 021 |  | 62 | S020NDA30CL021 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA30-BB010 | LP SGW Drum | Level | S020NDA30-BR333-80-CL4 | 80 | CL4 | LP SGW & Condensate | Full Vac | 6.5 | -5 | 143 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | CCI-DET-2704 NDA-MEC-DET-1053 | CCI-DAT-1467 | PRO-PID-0014 | Replaced 3"/DN80 CL 150 | 7 | Custom Controls | Rosemount | 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
49 | TH00 | S02 | 0NDA | 30 | LIT | DL | 022 |  | 63 | S020NDA30CL022 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA30-BB010 | LP SGW Drum | Level | S020NDA30-BR332-80-CL4 | 80 | CL4 | LP SGW & Condensate | Full Vac | 6.5 | -5 | 143 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | CCI-DET-2704 NDA-MEC-DET-1053 | CCI-DAT-1467 | PRO-PID-0014 | Replaced 3"/DN80 CL 150 | 7 | Custom Controls | Rosemount | 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
50 | TH00 | S02 | 0NDA | 30 | LIT | DL | 023 |  | 64 | S020NDA30CL023 | Level Transmitter (DP) | Separation Plant | Production Piping System | S020NDA30-BB010 | LP SGW Drum | Level | S020NDA30-BR331-80-CL4 | 80 | CL4 | LP SGW & Condensate | Full Vac | 6.5 | -5 | 143 | - | - | mm | 0 to 2680 | 1676 | 335 to 3015 | CCI-DET-2704 NDA-MEC-DET-1053 | CCI-DAT-1467 | PRO-PID-0014 | Replaced 3"/DN80 CL 150 | 7 | Custom Controls | Rosemount | 2051CD3A22A1BS2M4Q4Q8Q15+1199WDA94AFFW72DA00Q15+1199MDC56AFFW72DA00Q15 | 4500200843 | ETA 28/06/2023
51 | TH00 | S02 | 0NDA | 30 | LG | CL | 031 |  | 65 | S020NDA30CL031 | Level Gauge | Separation Plant | Production Piping System | S020NDA30-BB010 | LP SGW Drum | Level | S020NDA30-BR331-80-CL4 | 80 | CL4 | LP SGW & Condensate | Full Vac | 6.5 | -5 | 143 | - | - | mm | - | 1676 | 335 to 3018 | CCI-DET-2705 NDA-MEC-DET-1053 | CCI-DAT-1471 | PRO-PID-0014 | 2"/DN50 CL150 Verify bridle nozzle dimension with vessel manufacturer. | 6 | Powerflo Solutions | Bliss Anand | R/88/M/S/2/1/B/N/N/X/PN/S/2560MM/20/S/S/P/FLG/X/1/3/NA/21+71+81 | 4500193407 | 2023-03-24
43 | TH00 | S02 | 0NDA | 30 | PIT | CP | 011 |  | 55 | S020NDA30CP011 | Pressure Indicating Transmitter | Separation Plant | Production Piping System | S020NDA30-AT010 | LP Separator A Inlet | Pressure | S020NDA30-BR021-1050-CL1 | 1050 | CL1 | LP Two Phase | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 |  | 6.2 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
44 | TH00 | S02 | 0NDA | 30 | PIT | CP | 012 |  | 56 | S020NDA30CP012 | Pressure Indicating Transmitter | Separation Plant | Production Piping System | S020NDA30-AT020 | LP Separator B Inlet | Pressure | S020NDA30-BR023-1050-CL1 | 1050 | CL1 | LP Two Phase | Full Vac | 5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 1 | 0 to 5 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0014 |  | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
112 | TH00 | S02 | 0NDB | 10 | PIT | CP | 010 |  | 1 | S020NDB10CP010 | Pressure Indicating Transmitter | Separation Plant | Separated Water System |  | SGW Reinjection Pump Station Inlet | Pressure | S020NDB10-BR010-900-CL4 | 900 | CL4 | LP SGW & Condensate | Full Vac | 6.5 | -5 | 143 | - | - | bar(g) | -1 to 10.3 | 2.6 | 0 to 10 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0026 |  | 3.7 | Custom Controls | Rosemount | 2051TG2A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-01
406 | TH00 | S02 | 0NDB | 11 | FIT | CF | 011 |  | 182 | S020NDB11CF011 | Flow Transmitter (Magnetic) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Flow | S020NDB11-BR601-15-S10 | 15 | S10 | SGW Condensate | Full Vac | 10 | -5 | 75 | 0 | Refer to Specification | l/m | Refer to Specification | Refer to Specification | 0 to 10 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Note 1 | 5.6 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | 4500192700 | 2022-11-10
405 | TH00 | S02 | 0NDB | 11 | AT | CQ | 010 |  | 181 | S020NDB11CQ010 | Analyser Transmitter (pH) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | pH | S020NDB11-BR601-15-S10 | 15 | S10 | SGW Condensate | Full Vac | 10 | -5 | 75 | - | - | pH | 0 to 14 | 5 | 3.5 to 8.5 | Vendor Designed | QCM-PRO-DAT-0108 | PRO-PID-0100 | Note 1 |  | EMC | E+H | CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 + CPA-C111 + Cover | 4500191501 | 2022-11-10
404 | TH00 | S02 | 0NDB | 11 | TIT | CT | 011 |  | 180 | S020NDB11CT011 | Temperature Indicating Transmitter | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | S020NDB11-BR601-15-S10 | 15 | S10 | SGW Condensate | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 75 | 60 | 0 to 100 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Note 1, Note 7 | 4.6 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8R21XW | 4500192700 | 2023-01-12
410 | TH00 | S02 | 0NDB | 12 | FIT | CF | 021 |  | 186 | S020NDB12CF021 | Flow Transmitter (Magnetic) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Flow | S020NDB12-BR602-15-S10 | 15 | S10 | SGW Condensate | Full Vac | 10 | -5 | 75 | 0 | Refer to Specification | l/m | Refer to Specification | Refer to Specification | 0 to 10 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Note 1 | 5.6 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | 4500192700 | 2022-11-10
409 | TH00 | S02 | 0NDB | 12 | AT | CQ | 020 |  | 185 | S020NDB12CQ020 | Analyser Transmitter (pH) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | pH | S020NDB12-BR602-15-S10 | 15 | S10 | SGW Condensate | Full Vac | 10 | -5 | 75 | - | - | pH | 0 to 14 | 5 | 3.5 to 8.5 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Note 1 |  | EMC | E+H | CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 + CPA-C111 + Cover | 4500191501 | 2022-11-10
408 | TH00 | S02 | 0NDB | 12 | TIT | CT | 021 |  | 184 | S020NDB12CT021 | Temperature Indicating Transmitter | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | S020NDB12-BR602-15-S10 | 15 | S10 | SGW Condensate | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 75 | 60 | 0 to 100 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Note 1, Note 7 | 4.6 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8R21XW | 4500192700 | 2023-01-12
414 | TH00 | S02 | 0NDB | 13 | FIT | CF | 031 |  | 190 | S020NDB13CF031 | Flow Transmitter (Magnetic) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Flow | S020NDB13-BR603-15-S10 | 15 | S10 | SGW Condensate | Full Vac | 10 | -5 | 75 | 0 | Refer to Specification | l/m | Refer to Specification | Refer to Specification | 0 to 10 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Note 1 | 5.6 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | 4500192700 | 2022-11-10
413 | TH00 | S02 | 0NDB | 13 | AT | CQ | 030 |  | 189 | S020NDB13CQ030 | Analyser Transmitter (pH) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | pH | S020NDB13-BR603-15-S10 | 15 | S10 | SGW Condensate | Full Vac | 10 | -5 | 75 | - | - | pH | 0 to 14 | 5 | 3.5 to 8.5 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Note 1 |  | EMC | E+H | CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 + CPA-C111 + Cover | 4500191501 | 2022-11-10
412 | TH00 | S02 | 0NDB | 13 | TIT | CT | 031 |  | 188 | S020NDB13CT031 | Temperature Indicating Transmitter | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | S020NDB13-BR603-15-S10 | 15 | S10 | SGW Condensate | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 75 | 60 | 0 to 100 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Note 1, Note 7 | 4.6 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8R21XW | 4500192700 | 2023-01-12
418 | TH00 | S02 | 0NDB | 14 | FIT | CF | 041 |  | 194 | S020NDB14CF041 | Flow Transmitter (Magnetic) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Flow | S020NDB14-BR604-15-S10 | 15 | S10 | SGW Condensate | Full Vac | 10 | -5 | 75 | 0 | Refer to Specification | l/m | Refer to Specification | Refer to Specification | 0 to 10 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Note 1 | 5.6 | Custom Controls | Rosemount | 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | 4500192700 | 2022-11-10
417 | TH00 | S02 | 0NDB | 14 | AT | CQ | 040 |  | 193 | S020NDB14CQ040 | Analyser Transmitter (pH) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | pH | S020NDB14-BR604-15-S10 | 15 | S10 | SGW Condensate | Full Vac | 10 | -5 | 75 | - | - | pH | 0 to 14 | 5 | 3.5 to 8.5 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Note 1 |  | EMC | E+H | CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 + CPA-C111 + Cover | 4500191501 | 2022-11-10
416 | TH00 | S02 | 0NDB | 14 | TIT | CT | 041 |  | 192 | S020NDB14CT041 | Temperature Indicating Transmitter | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | S020NDB14-BR604-15-S10 | 15 | S10 | SGW Condensate | Full Vac | 10 | -5 | 75 | - | - | °C | 0 to 75 | 60 | 0 to 100 | Vendor Designed | QCM-PRO-SPC-0109 | PRO-PID-0100 | Note 1, Note 7 | 4.6 | Custom Controls | Rosemount | 644HANAJ1M4Q4T1+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8R21XW | 4500192700 | 2023-01-12
201 | TH00 | S02 | 0QCM | 10 | LIT | DL | 010 |  | 133 | S020QCM10CL010 | Level Transmitter (Radar) | Separation Plant | Acid Dosing System | S020QCM10-BB010 | Sulphuric Acid Storage Tank | Level | N/A | 50 | S1 | Low Pressure Sulphuric Acid | Full Vac | 5 | -5 | 50 | - | - | mm | 0 to 4500 | N/A | 0 to 100% | Nozzle mount QCM-PRO-DAT-0071 | CCI-DAT-1468 | PRO-PID-0029 | Tank manufacturer to finalise tank height. 2"/DN50 CL150 | 6.5 | Instrumatics | Vega | PS31.XXXXXGMHB +GFLK.ADGX | 4500189544 | 2022-11-10
202 | TH00 | S02 | 0QCM | 10 | LIT | DL | 020 |  | 134 | S020QCM10CL020 | Level Transmitter (Radar) | Separation Plant | Acid Dosing System | S020QCM10-BB010 | Sulphuric Acid Storage Tank | Level | N/A | 50 | S1 | Low Pressure Sulphuric Acid | Full Vac | 5 | -5 | 50 | - | - | mm | 0 to 4500 | N/A | 0 to 100% | Nozzle mount QCM-PRO-DAT-0071 | CCI-DAT-1468 | PRO-PID-0029 | Tank manufacturer to finalise tank height. 2"/DN50 CL150 | 6.5 | Instrumatics | Vega | PS31.XXXXXGMHB +GFLK.ADGX | 4500189544 | 2022-11-10
203 | TH00 | S02 | 0QCM | 10 | TE | CT | 010 |  | 137 | S020QCM10CT010 | Temperature Element | Separation Plant | Acid Dosing System | S020QCM10-BB010 | Sulphuric Acid Storage Tank | Temperature | N/A | N/A | S1 | Low Pressure Sulphuric Acid | Full Vac | 5 | -5 | 50 | - | - | °C | -5 to 50 | 20 | -5 to 50 | CCI-DET-2703 QCM-PRO-DAT-0071 | CCI-DAT-1466 | PRO-PID-0029 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0155SLAR1C2B1UAE065TBXW+114CM0080TAC2SC075AQ5Q8R21XW | 4500191995 | 2022-11-10
171 | TH00 | S02 | 0QCM | 10 | LI | DL | 0020 |  | 135 | S020QCM10DL0020 | Level Indicator (Remote) | Separation Plant | Acid Dosing System | S020QCM10-BB010 | Sulphuric Acid Storage Tank | Level | N/A | N/A | N/A | - | atm | atm | -5 | 50 | - | - | mm | See notes | N/A | 0-100% | CCI-DET-2720 | CCI-DAT-1470 | PRO-PID-0029 | Tank manufacturer to finalise tank height | 3.2 | Instrumatics | Vega | TKALM3-HMI-DB | 4500189544 | 2022-11-10
[9 empty] | 136 | S020QCM10EH011 | Level Sounder Beacon (Remote) | Separation Plant | Acid Dosing System | S020QCM10-BB010 | Sulphuric Acid Storage Tank | Level | N/A | N/A | N/A | - | atm | atm | -5 | 50 | - | - | mm | N/A | N/A | N/A | CCI-DET-2720 | See notes | PRO-PID-0029 | Indicator with sounder. Refer to Installation Drawaing | 3.2 | Instrumatics | Vega | See S020QCM10DL0020 | 4500189544 | 2022-11-10
219 | TH00 | S02 | 0QCM | 20 | FIT | DF | 010 |  | 155 | S020QCM20CF010 | Flow Transmitter (Magnetic) | Separation Plant | Acid Dosing System | S020QCM20-AP010 | Acid Dosing Pump A Outlet | Flow | S020QCM20-BR011-15-S2 | 15 | S2 | High Pressure Sulphuric Acid | Full Vac | 30 | -5 | 50 | 0 | 3 | l/m | 0-3 | 2.2 | 0 to 2.5 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0030 | Replaced 5mm, /DN15 CL300 | 7.1 | Yokogawa | Yokogawa | AX005-GA000BA2AT224B-2JA11/GRT | 4500201023 | ETA 2/10/2023
218 | TH00 | S02 | 0QCM | 20 | PIT | CP | 011 |  | 154 | S020QCM20CP011 | Pressure Indicating Transmitter | Separation Plant | Acid Dosing System | S020QCM20-AP010 | Acid Dosing Pump A Outlet | Pressure | S020QCM20-BR011-25-S2 | 25 | S2 | High Pressure Sulphuric Acid | Full Vac | 30 | -5 | 50 | - | - | bar(g) | -1 to 55 | 18.4 | 0 to 30 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0030 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
215 | TH00 | S02 | 0QCM | 20 | PI | CP | 501 |  | 151 | S020QCM20CP501 | Pressure Gauge | Separation Plant | Acid Dosing System | S020QCM20-AP010 | Acid Dosing Pump A Inlet | Pressure | S020QCM20-BR010-50-S2 | 50 | S2 | High Pressure Sulphuric Acid | Full Vac | 30 | -5 | 50 | - | - | bar(g) | 0 to 5 | 0.3 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0030 |  | 3.2 | Wika | Wika | 72039899+14503369+ | 4500189704 | 2022-11-10
216 | TH00 | S02 | 0QCM | 20 | PI | CP | 510 |  | 152 | S020QCM20CP510 | Pressure Gauge | Separation Plant | Acid Dosing System | S020QCM20-AP010 | Acid Dosing Pump A Outlet | Pressure | S020QCM20-BR011-25-S2 | 25 | S2 | High Pressure Sulphuric Acid | Full Vac | 30 | -5 | 50 | - | - | bar(g) | 0 to 40 | 18.4 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0030 |  | 3.2 | Wika | Wika | 72039915+14503369+ | 4500189704 | 2022-11-10
217 | TH00 | S02 | 0QCM | 20 | TE | CT | 010 |  | 153 | S020QCM20CT010 | Temperature Element | Separation Plant | Acid Dosing System | S020QCM20-AP010 | Acid Dosing Pump A Outlet | Temperature | S020QCM20-BR011-25-S2 | 25 | S2 | High Pressure Sulphuric Acid | Full Vac | 30 | -5 | 50 | - | - | °C | -5 to 50 | 20 | -5 to 50 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0030 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW | 4500191995 | 2023-01-12
| TH00 | S02 | 0QCM | 21 | FIT | DF | 020 |  | 160 | S020QCM21CF010Temp | Flow Transmitter (Magnetic) | Separation Plant | Acid Dosing System | S020QCM21-AP020 | Acid Dosing Pump B Outlet | Flow | S020QCM21-BR021-15-S2 | 15 | S2 | High Pressure Sulphuric Acid | Full Vac | 30 | -5 | 50 | 0 | 3 | l/m | 0-3 | 2.2 | 0 to 2.5 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0030 | Replaced 5mm, /DN15 CL300 | 7 | IFM | IFM | SI5004+E40107 | 4500200797 | 2023-05-10
224 | TH00 | S02 | 0QCM | 21 | FIT | DF | 020 |  | 160 | S020QCM21CF020 | Flow Transmitter (Magnetic) | Separation Plant | Acid Dosing System | S020QCM21-AP020 | Acid Dosing Pump B Outlet | Flow | S020QCM21-BR021-15-S2 | 15 | S2 | High Pressure Sulphuric Acid | Full Vac | 30 | -5 | 50 | 0 | 3 | l/m | 0-3 | 2.2 | 0 to 2.5 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0030 | Replaced 5mm, /DN15 CL300 | 7.1 | Yokogawa | Yokogawa | AX005-GA000BA2AT224B-2JA11/GRT | 4500201023 | ETA 2/10/2023
| TH00 | S02 | 0QCM | 21 | FIT | DF | 020 |  | 160 | S020QCM21CF020Temp | Flow Transmitter (Magnetic) | Separation Plant | Acid Dosing System | S020QCM21-AP020 | Acid Dosing Pump B Outlet | Flow | S020QCM21-BR021-15-S2 | 15 | S2 | High Pressure Sulphuric Acid | Full Vac | 30 | -5 | 50 | 0 | 3 | l/m | 0-3 | 2.2 | 0 to 2.5 | CCI-DET-2707 | CCI-DAT-1474 | PRO-PID-0030 | Replaced 5mm, /DN15 CL300 | 7 | IFM | IFM | SI5004+E40107 | 4500200797 | 2023-05-10
223 | TH00 | S02 | 0QCM | 21 | PIT | CP | 021 |  | 159 | S020QCM21CP021 | Pressure Indicating Transmitter | Separation Plant | Acid Dosing System | S020QCM21-AP020 | Acid Dosing Pump B Outlet | Pressure | S020QCM21-BR021-25-S2 | 25 | S2 | High Pressure Sulphuric Acid | Full Vac | 30 | -5 | 50 | - | - | bar(g) | -1 to 55 | 18.4 | 0 to 30 | CCI-DET-2700 | CCI-DAT-1461 | PRO-PID-0030 |  | 3.8 | Custom Controls | Rosemount | 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | 4500191995 | 2022-12-20
220 | TH00 | S02 | 0QCM | 21 | PI | CP | 502 |  | 156 | S020QCM21CP502 | Pressure Gauge | Separation Plant | Acid Dosing System | S020QCM21-AP020 | Acid Dosing Pump B Inlet | Pressure | S020QCM21-BR020-50-S2 | 50 | S2 | High Pressure Sulphuric Acid | Full Vac | 30 | -5 | 50 | - | - | bar(g) | 0 to 5 | 0.3 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0030 |  | 3.2 | Wika | Wika | 72039899+14503369+ | 4500189704 | 2022-11-10
221 | TH00 | S02 | 0QCM | 21 | PI | CP | 520 |  | 157 | S020QCM21CP520 | Pressure Gauge | Separation Plant | Acid Dosing System | S020QCM21-AP020 | Acid Dosing Pump B Outlet | Pressure | S020QCM21-BR021-25-S2 | 25 | S2 | High Pressure Sulphuric Acid | Full Vac | 30 | -5 | 50 | - | - | bar(g) | 0 to 40 | 18.4 | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0030 |  | 3.2 | Wika | Wika | 72039915+14503369+ | 4500189704 | 2022-11-10
222 | TH00 | S02 | 0QCM | 21 | TE | CT | 020 |  | 158 | S020QCM21CT020 | Temperature Element | Separation Plant | Acid Dosing System | S020QCM21-AP020 | Acid Dosing Pump B Outlet | Temperature | S020QCM21-BR021-25-S2 | 25 | S2 | High Pressure Sulphuric Acid | Full Vac | 30 | -5 | 50 | - | - | °C | -5 to 50 | 20 | -5 to 50 | CCI-DET-2703 MEC-DET-1031 | CCI-DAT-1466 | PRO-PID-0030 | Note 7 | 6.6 | Custom Controls | Rosemount | 214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAC2SC075AQ35Q5Q8XW | 4500191995 | 2022-11-10
204 | TH00 | S02 | 0QCM | 30 | LIT | DL | 031 |  | 138 | S020QCM30CL031 | Level Transmitter (Radar) | Separation Plant | Acid Dosing System | S020QCM30-AP010 | Sulphuric Acid Dosing System Sump Pump | Level | N/A | N/A | N/A | Low Pressure Sulphuric Acid | atm | atm | -5 | 50 | - | - | mm | 0 to 1500 | N/A | 0 to 1500 | CCI-DET-2706 | CCI-DAT-1468 | PRO-PID-0029 | Bracket mount | 3.2 | Instrumatics | Vega | PS21.XXXXXGMHB+MBA.BB | 4500189544 | 2022-11-10
205 | TH00 | S02 | 0QCM | 30 | LIT | DL | 032 |  | 139 | S020QCM30CL032 | Level Transmitter (Radar) | Separation Plant | Acid Dosing System | S020QCM30-AP010 | Sulphuric Acid Dosing System Sump Pump | Level | N/A | N/A | N/A | Low Pressure Sulphuric Acid | atm | atm | -5 | 50 | - | - | mm | 0 to 1500 | N/A | 0 to 1500 | CCI-DET-2706 | CCI-DAT-1468 | PRO-PID-0029 | Bracket mount | 3.2 | Instrumatics | Vega | PS21.XXXXXGMHB+MBA.BB | 4500189544 | 2022-11-10
206 | TH00 | S02 | 0QCM | 30 | AIT | DQ | 010 |  | 140 | S020QCM30CQ010 | Analyser Transmitter (Conductivity) | Separation Plant | Acid Dosing System | S020QCM30-AP010 | Sulphuric Acid Dosing System Sump Pump | pH | N/A | N/A | N/A | Low Pressure Sulphuric Acid | atm | atm | -5 | 50 | - | - | uS/cm | TBC | TBC | TBC | See notes | See notes | PRO-PID-0029 | CEL to specifiy to match Te Mihi | 5.6 | EMC | E+H | CLS50D-1009/0 + CYA112-1V02/0 + CM442 CM442-2ER8/0 | 4500191348 | 2022-11-10
| TH00 | S02 | 0SGA | 10 | PI | CP | 401 |  |  | S020SGA10CP401 | Pressure Gauge | Pump Station | Fire Water | S020GAC30-CF042 | Fire Water | Pressure |  | 20 | S9 | Seal Water | Full Vac | 16 | -5 | 50 | - | - | bar(g) | 0 to 16 |  | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0050 |  |  | Wika | Wika | 72039878+14503369 | 4500193000
| TH00 | S02 | 0SGA | 10 | PI | CP | 402 |  |  | S020SGA10CP402 | Pressure Gauge | Pump Station | Fire Water | S020GAC30-CF042 | Fire Water | Pressure |  | 20 | S9 | Seal Water | Full Vac | 16 | -5 | 50 | - | - | bar(g) | 0 to 16 |  | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0050 |  |  | Wika | Wika | 72039878+14503369 | 4500193000
| TH00 | S02 | 0SGA | 10 | PI | CP | 405 |  |  | S020SGA10CP405 | Pressure Gauge | Pump Station | Fire Water | S020GAC30-CF042 | Fire Water | Pressure |  | 20 | S9 | Seal Water | Full Vac | 16 | -5 | 50 | - | - | bar(g) | 0 to 16 |  | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0050 |  |  | Wika | Wika | 72039878+14503369 | 4500193000
| TH00 | S02 | 0SGA | 10 | PI | CP | 406 |  |  | S020SGA10CP406 | Pressure Gauge | Pump Station | Fire Water | S020GAC30-CF042 | Fire Water | Pressure |  | 20 | S9 | Seal Water | Full Vac | 16 | -5 | 50 | - | - | bar(g) | 0 to 16 |  | - | CCI-DET-2701 | CCI-DAT-1460 | PRO-PID-0050 |  |  | Wika | Wika | 72039878+14503369 | 4500193000
| TH00 | S02 | 0SAA | 10 | TE |  |  |  |  | S020SAA10CT001 | Temperature Element | Separation Plant | Room Temperature |  |  | Temperature | [18 empty] | 6.3 | EMC | E+H | TST434-J1A3B0 | 4500199015 | 2023-04-06
| TH00 | S02 | 0SAA | 10 | TE |  |  |  |  | S020SAA10CT002 | Temperature Element | Separation Plant | Room Temperature |  |  | Temperature | [18 empty] | 6.3 | EMC | E+H | TST434-J1A3B0 | 4500199015 | 2023-04-06
| TH00 | S02 | 0SAA | 10 | TE |  |  |  |  | S020SAA10CT003 | Temperature Element | Separation Plant | Room Temperature |  |  | Temperature | [18 empty] | 6.3 | EMC | E+H | TST434-J1A3B0 | 4500199015 | 2023-04-06
| TH00 | PO2 | 0SAA | 10 | TE |  |  |  |  | P020SAA10CT001 | Temperature Element | Pump Station | Room Temperature |  |  | Temperature | [18 empty] | 6.3 | EMC | E+H | TST434-J1A3B0 | 4500199015 | 2023-04-06
| TH00 | PO2 | 0SAA | 10 | TE |  |  |  |  | P020SAA10CT002 | Temperature Element | Pump Station | Room Temperature |  |  | Temperature | [18 empty] | 6.3 | EMC | E+H | TST434-J1A3B0 | 4500199015 | 2023-04-06
| TH00 | PO2 | 0SAA | 10 | TE |  |  |  |  | P020SAA10CT003 | Temperature Element | Pump Station | Room Temperature |  |  | Temperature | [18 empty] | 6.3 | EMC | E+H | TST434-J1A3B0 | 4500199015 | 2023-04-06
| TH00 | PO2 | 0SAA | 10 | TE |  |  |  |  | P020SAA10CT004 | Temperature Element | Pump Station | Room Temperature |  |  | Temperature | [18 empty] | 6.3 | EMC | E+H | TST434-J1A3B0 | 4500199015 | 2023-04-06
| TH00 | S02 | 0NDB | 11 | PI |  |  |  |  | S020NDB11AC010_QP01 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0100 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 11 | PI |  |  |  |  | S020NDB11AC010_QP02 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0100 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 11 | PI |  |  |  |  | S020NDB11AC010_QP03 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0100 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 12 | PI |  |  |  |  | S020NDB12AC020_QP01 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0100 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 12 | PI |  |  |  |  | S020NDB12AC020_QP02 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0100 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 12 | PI |  |  |  |  | S020NDB12AC020_QP03 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0100 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 13 | PI |  |  |  |  | S020NDB13AC030_QP01 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0100 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 13 | PI |  |  |  |  | S020NDB13AC030_QP02 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0100 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 13 | PI |  |  |  |  | S020NDB13AC030_QP03 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0100 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 14 | PI |  |  |  |  | S020NDB14AC040_QP01 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0100 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 14 | PI |  |  |  |  | S020NDB14AC040_QP02 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0100 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 14 | PI |  |  |  |  | S020NDB14AC040_QP03 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | LP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0100 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 23 | PI |  |  |  |  | S020NDA23AC010_QP01 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | HP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0101 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 23 | PI |  |  |  |  | S020NDA23AC010_QP02 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | HP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0101 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 23 | PI |  |  |  |  | S020NDA23AC010_QP03 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | HP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0101 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 24 | PI |  |  |  |  | S020NDA24AC020_QP01 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | HP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0101 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 24 | PI |  |  |  |  | S020NDA24AC020_QP02 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | HP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0101 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
| TH00 | S02 | 0NDB | 24 | PI |  |  |  |  | S020NDA24AC020_QP03 | Temperature Indicator (Gauge) | Separation Plant | Separated Water System | - | HP SGW pH Monitoring Skid | Temperature | [16 empty] | PRO-PID-0101 |  | 7.5 | Vendor Supplied | Vendor Supplied | Vendor Supplied | Vendor Supplied
Note on N123: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Seal Water System until row 342
Note on F144: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To confirm iff TT are now to be changed to TIT.
Note on F145: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To confirm iff TT are now to be changed to TIT.
Note on F146: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To confirm iff TT are now to be changed to TIT.
Note on F147: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To confirm iff TT are now to be changed to TIT.
Note on F177: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To confirm iff TT are now to be changed to TIT.

## Well
Service Properties
General Notes:
1. Two-Phase flow calculation undertaken in control system with DP and Static pressure instrument process variable signals from instrument.
2. CEL to provide orifice plate sizing for two-phase flow meter.
3. Flow element to be conditioning type to minimize upstream and downstream straight lengths.
4. Reverse flow detection required for reinjection flow transmitters.
5. For Pipe Specification Information Refer to TABG-JEC-0-000-PRO-PID-0002.
6. Flanged instruments shall be ASME B16.5 unless otherwise specified.
7. Wake frequency calculations to be performed for all thermowells and corrosometers. Instrument vendor to confirm insertion length based on calculations and pipe dimension.
8. Square root extraction within DP instrument to output linearised flow measurement.

## SEP
Service Properties
General Notes:
1. Supplied with Equipment. To be confirmed with equipment Supplier.
2. SIL rated instrument with yellow coloured body.
3. Flow element to be conditioning type to minimize upstream and downstream straight lengths.
4. -
5. For Pipe Specification Information Refer to TABG-JEC-0-000-PRO-PID-0002.
6. Flanged instruments shall be ASME B16.5 unless otherwise specified.
7. Wake frequency calculations to be performed for all thermowells and corrosometers. Instrument vendor to confirm insertion length based on calculations and pipe dimension.
8. Square root extraction within DP instrument to output linearised flow measurement output.

## SGW
Service Properties
General Notes:
1. Supplied with Equipment. To be confirmed with equipment Supplier.
2. -
3. Flow element to be conditioning type to minimize upstream and downstream straight lengths.
4. -
5. For Pipe Specification Information Refer to TABG-JEC-0-000-PRO-PID-0002.
6. Flanged instruments shall be ASME B16.5 unless otherwise specified.
7. Wake frequency calculations to be performed for all thermowells. Instrument vendor to confirm insertion length based on calculations and pipe dimension.
8. Square root extraction within DP instrument to output linearised flow measurement output.