## Sheet1
| Station | System | Tag | Funct | Type | Criticality | ResCon | PECPR | NominalValue | Range | Point | DeviceType | Setting | Proof | PlantCode | Data (CCI-DAT-) | StoresNo | DrawingNo | Procs | MVUnit | IdealUnit | Checked | DateChecked | CheckedBy | Changed | CalcErr | MVar1 | MVar2 | MVar3 | MVar4 | MVar5 | MVar6 | IdO1 | IdO2 | IdO3 | IdO4 | IdO5 | IdO6 | MVar7 | IdO7 | Digi1 | Digi2 | Digi3 | Digi4 | Digi5 | Digi6 | KPI | DigiAliase1 | DigiAliase2 | DigiAliase3 | DigiAliase4 | DigiAliase5 | DigiAliase6
0 | Tauhara B Steamfield | Wellpad TH11 Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | C | FALSE | FALSE | - | 2200 to 6000 | Wellpad TH11 - Level | -edit- | 2200 to 6000 | +/- 1% | TH000110LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-33 | rev: 7.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 2200 | 3150 | 4100 | 5050 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | FALSE
1 | Tauhara B Steamfield | Wellpad TH11 Condensate System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B | FALSE | FALSE | 550 | -10 to 1500 | Wellpad TH11 - Flow | -edit- | 0 to 1500 | +/- 1% | TH000110NAB10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-33 | rev: 7.8 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # 0110NAB10-BR010-300-S12 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 375 | 750 | 1125 | 1500 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
2 | Tauhara B Steamfield | Wellpad TH11 Condensate System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B | FALSE | FALSE | 5.1 | -1 to 55 | Wellpad TH11 - Pressure | -edit- | 0 to 25 | +/- 1% | TH000110NAB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-33 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 20 | [5 empty] | FALSE
3 | Tauhara B Steamfield | Wellpad TH11 Condensate System | 10CP510 | - | Wika 72039878+14503369+0731277 | C | FALSE | FALSE | 5.1 | 0 to 25 | Wellpad TH11 - Pressure | -edit- | - | +/- 1% | TH000110NAB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-33 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | FALSE
4 | Tauhara B Steamfield | Wellpad TH11 Condensate System | 10CP520 | - | Wika 72039878+14503369+0731277 | C | FALSE | FALSE | 5.1 | 0 to 25 | Wellpad TH11 - Pressure | -edit- | - | +/- 1% | TH000110NAB10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-33 | rev: 7.3 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0110NAB10-BR010-300-S12 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | FALSE
5 | Tauhara B Steamfield | Wellpad TH12 Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | C | FALSE | FALSE | 950 | 0 to 1300 | Wellpad TH12 - Level | -edit- | 0 to 1300 | +/- 1% | TH000120LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-37 | rev: 3.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: (LFC-)MEC-AGT-2099 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 325 | 650 | 975 | 1300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
6 | Tauhara B Steamfield | Wellpad TH12 Common Steam/Water Dump System | 10CL020 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | FALSE | FALSE | 2350 | 2200 to 6000 | Wellpad TH12 - Level | -edit- | 2200 to 6000 | +/- 1% | TH000120LFC10CL020 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-37 | rev: 7.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 2200 | 3150 | 4100 | 5050 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | FALSE
7 | Tauhara B Steamfield | Wellpad TH12 Common Steam/Water Dump System | 10CP010 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | C | FALSE | FALSE | 0 | -1 to 10.3 | Wellpad TH12 - Pressure | -edit- | 0 to 10 | +/- 1% | TH000120LFC10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-37 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # 0120LFC10-BR532-350-CL1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
8 | Tauhara B Steamfield | Wellpad TH12 Common Steam/Water Dump System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 30 | 0 to 100 | Wellpad TH12 - Pressure | -edit- | - | +/- 1% | TH000120LFC10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-37 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0120LFC10-BR530-250-CP1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
9 | Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CF010 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B | FALSE | FALSE | 699 | TBC | Wellpad TH12 - Flow | -edit- | TBC | +/- 1% | TH000120NDA10CF010 | CCI-DAT-1472 Note 2 | PO# 4500191995 | PRO-PID-37 | rev: 6.3 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # 0120NDA10-BR010-400-CP1 | tph (Note 1) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 192.5 | 385 | 577.5 | 770 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
10 | Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CP010 | - | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B | FALSE | FALSE | 0 | -1 to 276 | Wellpad TH12 - Pressure | -edit- | 0 to 75 | +/- 1% | TH000120NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-37 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 18.75 | 37.5 | 56.25 | 75 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | [5 empty] | FALSE
11 | Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CP510 | - | Wika 72039884+14503369+0763349 | C | FALSE | FALSE | 30 | 0 to 100 | Wellpad TH12 - Pressure | -edit- | - | +/- 1% | TH000120NDA10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-37 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
12 | Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CP520 | - | Wika 72039884+14503369+0763349 | C | FALSE | FALSE | 30 | 0 to 100 | Wellpad TH12 - Pressure | -edit- | - | +/- 1% | TH000120NDA10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-37 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0120NDA10-BR010-400-CP1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
13 | Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | C | FALSE | FALSE | 235 | 0 to 300 | Wellpad TH12 - Temperature | -edit- | 0 to 300 | +/- 1% | TH000120NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-37 | rev: 3.7 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # 0120NDA10-BR010-400-CP1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 75 | 150 | 225 | 300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
14 | Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CF010 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B | FALSE | FALSE | 699 | TBC | Wellpad TH12 (TH21) - Flow | -edit- | TBC | +/- 1% | TH000210NDA10CF010 | CCI-DAT-1472 Note 2 | PO# 4500191995 | PRO-PID-37 | rev: 6.3 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # 0210NDA10-BR010-400-CP1 | tph (Note 1) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 192.5 | 385 | 577.5 | 770 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
15 | Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CP010 | - | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B | FALSE | FALSE | 30 | -1 to 276 | Wellpad TH12 (TH21) - Pressure | -edit- | 0 to 75 | +/- 1% | TH000210NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-37 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 18.75 | 37.5 | 56.25 | 75 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | [5 empty] | FALSE
16 | Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 30 | 0 to 100 | Wellpad TH12 (TH21) - Pressure | -edit- | - | +/- 1% | TH000210NDA10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-37 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
17 | Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CP520 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 30 | 0 to 100 | Wellpad TH12 (TH21) - Pressure | -edit- | - | +/- 1% | TH000210NDA10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-37 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0210NDA10-BR010-400-CP1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
18 | Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 235 | 0 to 300 | Wellpad TH12 (TH21) - Temperature | -edit- | 0 to 300 | +/- 1% | TH000210NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-37 | rev: 4.8 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # 0210NDA10-BR010-400-CP1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 75 | 150 | 225 | 300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
19 | Tauhara B Steamfield | Wellpad TH26 Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | FALSE | FALSE | 950 | 0 to 1300 | Wellpad TH26 - Level | -edit- | 0 to 1300 | +/- 1% | TH000260LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-36 | rev: 3.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: (LFC-)MEC-AGT-2099 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 325 | 650 | 975 | 1300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
20 | Tauhara B Steamfield | Wellpad TH26 Common Steam/Water Dump System | 10CL020 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | FALSE | FALSE | 2350 | 2200 to 6000 | Wellpad TH26 - Level | -edit- | 2200 to 6000 | +/- 1% | TH000260LFC10CL020 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-36 | rev: 7.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 2200 | 3150 | 4100 | 5050 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | FALSE
21 | Tauhara B Steamfield | Wellpad TH26 Common Steam/Water Dump System | 10CP010 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 0 | -1 to 10.3 | Wellpad TH26 - Pressure | -edit- | 0 to 10 | +/- 1% | TH000260LFC10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-36 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # 0260LFC10-BR532-350-CL1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
22 | Tauhara B Steamfield | Wellpad TH26 Common Steam/Water Dump System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 30 | 0 to 100 | Wellpad TH26 - Pressure | -edit- | - | +/- 1% | TH000260LFC10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-36 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0260LFC10-BR530-250-CP1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
23 | Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CF010 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B | FALSE | FALSE | 699 | TBC | Wellpad TH26 - Flow | -edit- | TBC | +/- 1% | TH000260NDA10CF010 | CCI-DAT-1472 Note 2 | PO# 4500191995 | PRO-PID-36 | rev: 6.3 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # 0260NDA10-BR010-400-CP1 | tph (Note 1) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 192.5 | 385 | 577.5 | 770 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
24 | Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CP010 | - | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B | FALSE | FALSE | 0 | -1 to 276 | Wellpad TH26 - Pressure | -edit- | 0 to 75 | +/- 1% | TH000260NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-36 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 18.75 | 37.5 | 56.25 | 75 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | [5 empty] | FALSE
25 | Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 30 | 0 to 100 | Wellpad TH26 - Pressure | -edit- | - | +/- 1% | TH000260NDA10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-36 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
26 | Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CP520 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 30 | 0 to 100 | Wellpad TH26 - Pressure | -edit- | - | +/- 1% | TH000260NDA10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-36 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0260NDA10-BR010-400-CP1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
27 | Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 235 | 0 to 300 | Wellpad TH26 - Temperature | -edit- | 0 to 300 | +/- 1% | TH000260NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-36 | rev: 3.7 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # 0260NDA10-BR010-400-CP1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 75 | 150 | 225 | 300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
28 | Tauhara B Steamfield | Wellpad TH28 Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | FALSE | FALSE | 950 | 0 to 1300 | Wellpad TH28 - Level | -edit- | 0 to 1300 | +/- 1% | TH000280LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-31 | rev: 3.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: (LFC-)MEC-AGT-2099 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 325 | 650 | 975 | 1300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
29 | Tauhara B Steamfield | Wellpad TH28 Common Steam/Water Dump System | 10CL020 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | FALSE | FALSE | 2350 | 2200 to 6000 | Wellpad TH28 - Level | -edit- | 2200 to 6000 | +/- 1% | TH000280LFC10CL020 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-31 | rev: 7.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 2200 | 3150 | 4100 | 5050 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | FALSE
30 | Tauhara B Steamfield | Wellpad TH28 Common Steam/Water Dump System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 30 | 0 to 100 | Wellpad TH28 - Pressure | -edit- | - | +/- 1% | TH000280LFC10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-31 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0280LFC10-BR530-250-CP1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
31 | Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CF010 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B | FALSE | FALSE | 531 | TBC | Wellpad TH28 - Flow | -edit- | TBC | +/- 1% | TH000280NDA10CF010 | CCI-DAT-1472 Note 2 | PO# 4500191995 | PRO-PID-31 | rev: 6.3 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # 0280NDA10-BR010-400-CP1 | - | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | FALSE
32 | Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CP010 | - | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B | FALSE | FALSE | 26.3 | -1 to 276 | Wellpad TH28 - Pressure | -edit- | 0 to 75 | +/- 1% | TH000280NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-31 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 18.75 | 37.5 | 56.25 | 75 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | [5 empty] | FALSE
33 | Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 26.3 | 0 to 100 | Wellpad TH28 - Pressure | -edit- | - | +/- 1% | TH000280NDA10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-31 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
34 | Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CP520 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 20.5 | 0 to 100 | Wellpad TH28 - Pressure | -edit- | - | +/- 1% | TH000280NDA10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-31 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0280NDA10-BR010-400-CP1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
35 | Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 216 | 0 to 300 | Wellpad TH28 - Temperature | -edit- | 0 to 300 | +/- 1% | TH000280NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-31 | rev: 4.8 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # 0280NDA10-BR010-400-CP1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 75 | 150 | 225 | 300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
36 | Tauhara B Steamfield | Wellpad TH29 Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | FALSE | FALSE | - | 2200 to 6000 | Wellpad TH29 - Level | -edit- | 2200 to 6000 | +/- 1% | TH000290LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-32 | rev: 7.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 2200 | 3150 | 4100 | 5050 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | FALSE
37 | Tauhara B Steamfield | Wellpad TH29 Separated Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 550 | -5 to 605 | Wellpad TH29 - Flow | -edit- | 0 to 900 | +/- 1% | TH000290NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-32 | rev: 7.4 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # 0290NDB10-BR010-300-CR1 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - | -5 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
38 | Tauhara B Steamfield | Wellpad TH29 Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 15 | -1 to 55 | Wellpad TH29 - Pressure | -edit- | 0 to 50 | +/- 1% | TH000290NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-32 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
39 | Tauhara B Steamfield | Wellpad TH29 Separated Water System | 10CP510 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad TH29 - Pressure | -edit- | - | +/- 1% | TH000290NDB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
40 | Tauhara B Steamfield | Wellpad TH29 Separated Water System | 10CP520 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad TH29 - Pressure | -edit- | - | +/- 1% | TH000290NDB10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0290NDB10-BR010-300-CR1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
41 | Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CF010 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B | FALSE | FALSE | 699 | TBC | Wellpad TH26 (TH30) - Flow | -edit- | TBC | +/- 1% | TH000300NDA10CF010 | CCI-DAT-1472 Note 2 | PO# 4500191995 | PRO-PID-36 | rev: 6.3 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # 0300NDA10-BR010-400-CP1 | tph (Note 1) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 192.5 | 385 | 577.5 | 770 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
42 | Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CP010 | - | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B | FALSE | FALSE | 30 | -1 to 276 | Wellpad TH26 (TH30) - Pressure | -edit- | 0 to 75 | +/- 1% | TH000300NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-36 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 18.75 | 37.5 | 56.25 | 75 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | [5 empty] | FALSE
43 | Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 30 | 0 to 100 | Wellpad TH26 (TH30) - Pressure | -edit- | - | +/- 1% | TH000300NDA10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-36 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
44 | Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CP520 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 30 | 0 to 100 | Wellpad TH26 (TH30) - Pressure | -edit- | - | +/- 1% | TH000300NDA10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-36 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0300NDA10-BR010-400-CP1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
45 | Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 235 | 0 to 300 | Wellpad TH26 (TH30) - Temperature | -edit- | 0 to 300 | +/- 1% | TH000300NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-36 | rev: 3.7 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # 0300NDA10-BR010-400-CP1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 75 | 150 | 225 | 300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
46 | Tauhara B Steamfield | Wellpad TH29 (TH31) Separated Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B | FALSE | FALSE | 550 | -5 to 605 | Wellpad TH29 (TH31) - Flow | -edit- | 0 to 1400 | +/- 1% | TH000310NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-32 | rev: 7.4 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # 0310NDB10-BR010-300-CR1 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 100 | 200 | 300 | 400 | -5 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
47 | Tauhara B Steamfield | Wellpad TH29 (TH31) Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B | FALSE | FALSE | 15 | -1 to 55 | Wellpad TH29 (TH31) - Pressure | -edit- | 0 to 50 | +/- 1% | TH000310NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-32 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 45 | [5 empty] | FALSE
48 | Tauhara B Steamfield | Wellpad TH29 (TH31) Separated Water System | 10CP501 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad TH29 (TH31) - Pressure | -edit- | - | +/- 1% | TH000310NDB10CP501 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
49 | Tauhara B Steamfield | Wellpad TH29 (TH31) Separated Water System | 10CP520 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad TH29 (TH31) - Pressure | -edit- | - | +/- 1% | TH000310NDB10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0310NDB10-BR010-300-CR1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
50 | Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CF010 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B | FALSE | FALSE | 531 | TBC | Wellpad TH28 (TH34) - Flow | -edit- | TBC | +/- 1% | TH000360NDA10CF010 | CCI-DAT-1472 Note 2 | PO# 4500191995 | PRO-PID-31 | rev: 6.4 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # 0340NDA10-BR010-400-CP1 | tph (Note 1) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 147.5 | 295 | 442.5 | 590 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
51 | Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CF020 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 531 | TBC | Wellpad TH28 (TH34) - Flow | -edit- | TBC | +/- 1% | TH000360NDA10CF020 | CCI-DAT-1472 Note 2 | PO# 4500193492 | PRO-PID-31 | rev: 6.4 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # 0340NDA10-BR010-400-CP1 | tph (Note 1) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 147.5 | 295 | 442.5 | 590 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
52 | Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CP010 | - | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 26.3 | -1 to 276 | Wellpad TH28 (TH34) - Pressure | -edit- | 0 to 75 | +/- 1% | TH000360NDA10CP010 |  | PO# 4500191995 | PRO-PID-31 | rev: 6.4 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 18.75 | 37.5 | 56.25 | 75 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | [5 empty] | FALSE
53 | Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 26.3 | 0 to 100 | Wellpad TH28 (TH34) - Pressure | -edit- | - | +/- 1% | TH000360NDA10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-31 | rev: 6.4 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 |  | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
54 | Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CP520 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 20.5 | 0 to 100 | Wellpad TH28 (TH34) - Pressure | -edit- | - | +/- 1% | TH000360NDA10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-31 | rev: 6.4 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0340NDA10-BR010-400-CP1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 |  | 0 | 25 | 50 | 75 | 100 | [9 empty] | FALSE
55 | Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 216 | 0 to 300 | Wellpad TH28 (TH34) - Temperature | -edit- | 0 to 300 | +/- 1% | TH000360NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-31 | rev: 6.4 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # 0340NDA10-BR010-400-CP1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 75 | 150 | 225 | 300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
56 | Tauhara B Steamfield | Wellpad TH29 (TH35) Separated Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B | FALSE | FALSE | 15 | -5 to 605 | Wellpad TH29 (TH35) - Flow | -edit- | -5 to 200 | +/- 1% | TH000350NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-32 | rev: 7.4 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # EA30NDB10-BR010-300-CR1 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -5 | 46.25 | 97.5 | 148.75 | 200 | -5 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
57 | Tauhara B Steamfield | Wellpad TH29 (TEA-3) Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B | FALSE | FALSE | 30 | -1 to 55 | Wellpad TH29 (TEA-3) - Pressure | -edit- | 0 to 50 | +/- 1% | TH000350NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-32 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 45 | [5 empty] | FALSE
58 | Tauhara B Steamfield | Wellpad TH29 (TH35) Separated Water System | 10CP510 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 30 | 0 to 60 | Wellpad TH29 (TH35) - Pressure | -edit- | - | +/- 1% | TH000350NDB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
59 | Tauhara B Steamfield | Wellpad TH29 (TH35) Separated Water System | 10CP520 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad TH29 (TH35) - Pressure | -edit- | - | +/- 1% | TH000350NDB10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0350NDB10-BR010-300-CR1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
60 | Tauhara B Steamfield | Wellpad TH37 Separated Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B | FALSE | FALSE | 370 | 0 to 1000 | Wellpad TH37 - Flow | -edit- | 0 to 1000 | +/- 1% | TH000370NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-38 | rev: 7.4 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # 0370NDB10-BR010-300-CR1 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 250 | 500 | 750 | 1000 | -5 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
61 | Tauhara B Steamfield | Wellpad TH37 Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B | FALSE | FALSE | 15 | -1 to 55 | Wellpad TH37 - Pressure | -edit- | 0 to 50 | +/- 1% | TH000370NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-38 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 45 | [5 empty] | FALSE
62 | Tauhara B Steamfield | Wellpad TH37 Separated Water System | 10CP510 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad TH37 - Pressure | -edit- | - | +/- 1% | TH000370NDB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-38 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
63 | Tauhara B Steamfield | Wellpad TH37 Separated Water System | 10CP520 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad TH37 - Pressure | -edit- | - | +/- 1% | TH000370NDB10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-38 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0370NDB10-BR010-300-CR1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
64 | Tauhara B Steamfield | Wellpad TH37/38 Separated Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B | FALSE | FALSE | 370 | 0 to 1000 | Wellpad TH37/38 - Flow | -edit- | 0 to 1000 | +/- 1% | TH000380NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-38 |  | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 250 | 500 | 750 | 1000 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
65 | Tauhara B Steamfield | Wellpad TH37/38 Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B | FALSE | FALSE | 15 | -1 to 55 | Wellpad TH37/38 - Pressure | -edit- | 0 to 50 | +/- 1% | TH000380NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-38 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 45 | [5 empty] | FALSE
66 | Tauhara B Steamfield | Wellpad TH37/38 Separated Water System | 10CP501 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad TH37/38 - Pressure | -edit- | - | +/- 1% | TH000380NDB10CP501 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-38 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
67 | Tauhara B Steamfield | Wellpad TH37/38 Separated Water System | 10CP520 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad TH37/38 - Pressure | -edit- | - | +/- 1% | TH000380NDB10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-38 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 0380NDB10-BR010-300-CR1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
68 | Tauhara B Steamfield | TH12 Two Phase Pipeline Production Piping System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 21.27 | -1 to 55 | TH12 Two Phase Pipeline - Pressure | -edit- | 0 to 35 | +/- 1% | TH00L050NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-11 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # L050NDA10-BR030-750-CH1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 8.75 | 17.5 | 26.25 | 35 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 20 | [5 empty] | FALSE
69 | Tauhara B Steamfield | TH12 Two Phase Pipeline Production Piping System | 10CP532 | - | Wika 72039883+14503369+0763349 | - | FALSE | FALSE | 25 | 0 to 40 | TH12 Two Phase Pipeline - Pressure | -edit- | - | +/- 1% | TH00L050NDA10CP532 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-37 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # L050NDA10-BR30-750-CH1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 10 | 20 | 30 | 40 | 0 | 0 | 10 | 20 | 30 | 40 | [9 empty] | FALSE
70 | Tauhara B Steamfield | TH12 Two Phase Pipeline Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 217.9 | 0 to 250 | TH12 Two Phase Pipeline - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L050NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-11 | rev: 4.8 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # L050NDA10-BR030-750-CH1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
71 | Tauhara B Steamfield | TH12 Two Phase Pipeline Production Piping System | 10CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 215 | 0 to 250 | TH12 Two Phase Pipeline - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L050NDA10CT030 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-37 | rev: 4.8 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # L050NDA10-BR30-750-CH1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
72 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 21.27 | -1 to 55 | TH28 Two Phase Pipeline - Pressure | -edit- | 0 to 35 | +/- 1% | TH00L060NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-11 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # L060NDA10-BR030-800-CH1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 8.75 | 17.5 | 26.25 | 35 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 20 | [5 empty] | FALSE
73 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CP532 | - | Wika 72039884+14503369+0763349 | - | FALSE | FALSE | 20.5 | -1 to 55 | TH28 Two Phase Pipeline - Pressure | -edit- | 0 to 50 | +/- 1% | TH00L060NDA10CP532 | CCI-DAT-1460 | PO# 4500195012 | PRO-PID-31 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # 750 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 0 | 12.5 | 25 | 37.5 | 50 | [9 empty] | FALSE
74 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 217.9 | 0 to 250 | TH28 Two Phase Pipeline - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L060NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-11 | rev: 4.8 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # L060NDA10-BR030-800-CH1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
75 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 216 | 0 to 250 | TH28 Two Phase Pipeline - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L060NDA10CT030 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-31 | rev: 4.8 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # L060NDA10-BR030-750-CH1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
76 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT510 | - | Wika 72039934 (Model S5550/4) +72039931 (TW15-H) | - | FALSE | FALSE | 215 | 0 to 250 | TH28 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L060NDA10CT510 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 instment type: Temperature Indicator (Gauge) make: Wika Vendor: Wika drwg: CCI-DET-2703 line # L060NDA10-BR030-750-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
77 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT511 | - | Wika 72039935 Model S5550)+72039932 (Model TW15-H) | - | FALSE | FALSE | 215 | 0 to 250 | TH28 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L060NDA10CT511 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 instment type: Temperature Indicator (Gauge) make: Wika Vendor: Wika drwg: CCI-DET-2703 line # L060NDA10-BR450-200-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
78 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT520 | - | Wika 72039934 (Model S5550/4) +72039931 (TW15-H) | - | FALSE | FALSE | 215 | 0 to 250 | TH28 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L060NDA10CT520 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 instment type: Temperature Indicator (Gauge) make: Wika Vendor: Wika drwg: CCI-DET-2703 line # L060NDA10-BR030-800-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
79 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT521 | - | Wika 72040072 (Model S5550/4) +72040071 (TW15-H) | - | FALSE | FALSE | 215 | 0 to 250 | TH28 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L060NDA10CT521 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 instment type: Temperature Indicator (Gauge) make: Wika Vendor: Wika drwg: CCI-DET-2703 line # L060NDA10-BR460-100-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
80 | Tauhara B Steamfield | TH26 Two Phase Pipeline Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | FALSE | FALSE | - | 2200 to 6000 | TH26 Two Phase Pipeline - Level | -edit- | 2200 to 6000 | +/- 1% | TH00L070LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-34 | rev: 7.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 2200 | 3150 | 4100 | 5050 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | FALSE
81 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 21.27 | -1 to 55 | TH26 Two Phase Pipeline - Pressure | -edit- | 0 to 35 | +/- 1% | TH00L070NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-11 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # L070NDA10-BR030-800-CH1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 8.75 | 17.5 | 26.25 | 35 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 20 | [5 empty] | FALSE
82 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CP532 | - | Wika 72039883+14503369+0763349 | - | FALSE | FALSE | 25 | 0 to 40 | TH26 Two Phase Pipeline - Pressure | -edit- | - | +/- 1% | TH00L070NDA10CP532 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-36 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # L070NDA10-BR030-750-CH1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 10 | 20 | 30 | 40 | 0 | 0 | 10 | 20 | 30 | 40 | [9 empty] | FALSE
83 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 217.9 | 0 to 250 | TH26 Two Phase Pipeline - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L070NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-11 | rev: 4.8 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # L070NDA10-BR030-800-CH1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
84 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 215 | 0 to 250 | TH26 Two Phase Pipeline - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L070NDA10CT030 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-36 | rev: 4.8 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # L070NDA10-BR30-750-CH1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
85 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT510 | - | Wika 72039934 (Model S5550/4) +72039931 (TW15-H) | - | FALSE | FALSE | 215 | 0 to 250 | TH26 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L070NDA10CT510 | CCI-DAT-1463 |  | PRO-PID-34 |  | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
86 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT511 | - | Wika 72039934 (Model S5550/4) +72039931 (TW15-H) | - | FALSE | FALSE | 215 | 0 to 250 | TH26 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L070NDA10CT511 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 instment type: Temperature Indicator (Gauge) make: Wika Vendor: Wika drwg: CCI-DET-2703 line # L070NDA10-BR030-750-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
87 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT512 | - | Wika 72039935 Model S5550)+72039932 (Model TW15-H) | - | FALSE | FALSE | 215 | 0 to 250 | TH26 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L070NDA10CT512 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 instment type: Temperature Indicator (Gauge) make: Wika Vendor: Wika drwg: CCI-DET-2703 line # L070NDA10-BR440-200-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
88 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT522 | - | Wika 72040072 (Model S5550/4) +72040071 (TW15-H) | - | FALSE | FALSE | 215 | 0 to 250 | TH26 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L070NDA10CT522 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 instment type: Temperature Indicator (Gauge) make: Wika Vendor: Wika drwg: CCI-DET-2703 line # L070NDA10-BR450-100-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
89 | Tauhara B Steamfield | Condensate Pipeline To TH11 Condensate System | 10CP510 | - | Wika 72039879+14503369+0731277 | - | FALSE | FALSE | 5 | 0 to 16 | Condensate Pipeline To TH11 - Pressure | -edit- | - | +/- 1% | TH00L150NAB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-33 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # L150NAB10-BR010-630-S11 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4 | 8 | 12 | 16 | 0 | 0 | 4 | 8 | 12 | 16 | [9 empty] | FALSE
90 | Tauhara B Steamfield | SGW Pipeline To TH29 Well Pad Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 30 | -1 to 55 | SGW Pipeline To TH29 Well Pad - Pressure | -edit- | -1 to 50 | +/- 1% | TH00L190NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-35 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # L190NDB10-BR001-500-CR1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -1 | 11.75 | 24.5 | 37.25 | 50 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
91 | Tauhara B Steamfield | SWG Pipeline to TH29 Wellpad Separated Water System | 10CP011 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 15 | -1 to 55 | SWG Pipeline to TH29 Wellpad - Pressure | -edit- | 0 to 50 | +/- 1% | TH00L190NDB10CP011 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-32 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # L190NDB10-BR002-500-CR1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
92 | Tauhara B Steamfield | SWG Pipeline to TH29 Wellpad Separated Water System | 10CP510 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | SWG Pipeline to TH29 Wellpad - Pressure | -edit- | - | +/- 1% | TH00L190NDB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # L190NDB10-BR002-500-CR1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
93 | Tauhara B Steamfield | SWG Pipeline to TH29 Wellpad Separated Water System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 123 | 0 to 250 | SWG Pipeline to TH29 Wellpad - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L190NDB10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-32 | rev: 5.6 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # L190NDB10-BR002-500-CR1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
94 | Tauhara B Steamfield | SGW Pipeline To TH19N Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 30 | -1 to 55 | SGW Pipeline To TH19N - Pressure | -edit- | -1 to 50 | +/- 1% | TH00L200NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-35 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # L200NDB10-BR001-500-CR1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -1 | 11.75 | 24.5 | 37.25 | 50 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
95 | Tauhara B Steamfield | SGW Pipeline To Wellpad LCP Separated Water System | 10CP510 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | SGW Pipeline To Wellpad LCP - Pressure | -edit- | - | +/- 1% | TH00L210NDB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-38 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # L210NDB10-BR001-500-CR1 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
96 | Tauhara B Steamfield | SGW Pipeline To Wellpad LCP Separated Water System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 123 | 0 to 250 | SGW Pipeline To Wellpad LCP - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L210NDB10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-38 | rev: 5.6 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # L210NDB10-BR001-500-CR1 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
97 | Tauhara B Steamfield | Wellpad TH37 Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | FALSE | FALSE | - | 2200 to 6000 | Wellpad TH37 - Level | -edit- | 2200 to 6000 | +/- 1% | TH000370LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-38 | rev: 7.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 2200 | 3150 | 4100 | 5050 | 6000 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | FALSE
98 | Tauhara B Steamfield | Pump Station Seal Water System | 20CL010 | - | Rosemount 5408F1SHA2NA1R2ABCAA2M5DA1Q4Q8 | - | FALSE | FALSE |  | Note 9 | Pump Station - Level | -edit- | Note 9 | +/- 1% | TH00P020GWA20CL010 | CCI-DAT-1468 | PO# 4500191995 | PRO-PID-41 | rev: 5.6 instment type: Level Transmitter (Radar) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2706 PRO-DAT-0078 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
99 | Tauhara B Steamfield | Pump Station Seal Water System | 20CL011 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE |  | Note 9 | Pump Station - Level | -edit- | Refer to Notes | +/- 1% | TH00P020GWA20CL011 | CCI-DAT-1471 |  | PRO-PID-41 |  | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
100 | Tauhara B Steamfield | Pump Station Seal Water System | 20CL020 | - | Rosemount 5408F1SHA2NA1R2ABCAA2M5DA1Q4Q8 | - | FALSE | FALSE |  | Note 9 | Pump Station - Level | -edit- | Note 9 | +/- 1% | TH00P020GWA20CL020 | CCI-DAT-1468 | PO# 4500191995 | PRO-PID-41 | rev: 5.6 instment type: Level Transmitter (Radar) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2706 PRO-DAT-0078 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
101 | Tauhara B Steamfield | Pump Station Seal Water System | 20CL021 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE |  | Note 9 | Pump Station - Level | -edit- | Refer to Notes | +/- 1% | TH00P020GWA20CL021 | CCI-DAT-1471 |  | PRO-PID-41 |  | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
102 | Tauhara B Steamfield | Pump Station Potable Water System | 21CP520 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 3.49 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 10 | +/- 1% | TH00S020GKA21CP520 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-40 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2701 line # P020GKA21-BR043-50-S8 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 7.5 | [5 empty] | FALSE
103 | Tauhara B Steamfield | Pump Station Seal Water System | 20CP510 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA20CP510 | CCI-DAT-1460 |  | PRO-PID-41 |  | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
104 | Tauhara B Steamfield | Pump Station Seal Water System | 20CP511 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA20CP511 | CCI-DAT-1460 |  | PRO-PID-41 |  | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
105 | Tauhara B Steamfield | Pump Station Seal Water System | 30CP590 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA30CP590 | CCI-DAT-1460 |  | PRO-PID-41 |  | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
106 | Tauhara B Steamfield | Pump Station Seal Water System | 30CP591 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA30CP591 | CCI-DAT-1460 |  | PRO-PID-41 |  | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
107 | Tauhara B Steamfield | Pump Station Seal Water System | 30CT050 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 32 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020GWA30CT050 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-41 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # P020GAC30-BR072-50-S9 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 40 | [5 empty] | FALSE
108 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CL010 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | FALSE | FALSE | 773 | TBC | Pump Station - Level | -edit- | TBC | +/- 1% | TH00P020PCB20CL010 | CCI-DAT-1467 | PO# 4500191995 | PRO-PID-44 | rev: 5.6 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
109 | Tauhara B Steamfield | Pump Station Seal Water System | 21CP001 | - | Rosemount 2051CD3A02A1BS5M4Q4 | - | FALSE | FALSE | 0 | -2500 to 2500 | Pump Station - Pressure | -edit- | 0 to 250mbar | +/- 1% | TH00P020GWA21CP001 | CCI-DAT-1462 | PO# 4500191995 | PRO-PID-42 | rev: 4.0 instment type: Pressure Differential Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # P020GAC21-BR005-50-S9 | mbar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 200 |  | 50 |  |  |  | FALSE
110 | Tauhara B Steamfield | Pump Station Seal Water System | 21CP002 | - | Rosemount 2051TG1A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | -0.34 | -1 to 2.1 | Pump Station - Pressure | -edit- | -0.7 to +0.7 | +/- 1% | TH00P020GWA21CP002 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-42 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020GAC21-BR005-50-S9 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -0.7 | -0.35 | 0 | 0.35 | 0.7 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
111 | Tauhara B Steamfield | Pump Station Seal Water System | 22CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | - | FALSE | FALSE | 11.77 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 15 | +/- 1% | TH00P020GWA22CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-42 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020GAC21-BR023-50-S9 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
112 | Tauhara B Steamfield | Pump Station Seal Water System | 22CP510 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA22CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-42 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # P020GAC21-BR026-50-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
113 | Tauhara B Steamfield | Pump Station Seal Water System | 30CF010 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | FALSE | FALSE | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA30CF010 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 line # S020GAC30-BR031-20-S9 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | FALSE
114 | Tauhara B Steamfield | Pump Station Seal Water System | 30CF011 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | FALSE | FALSE | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA30CF011 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 line # S020GAC30-BR032-20-S9 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | FALSE
115 | Tauhara B Steamfield | Pump Station Seal Water System | 31CF020 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | FALSE | FALSE | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA31CF020 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 line # S020GAC30-BR041-20-S9 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | FALSE
116 | Tauhara B Steamfield | Pump Station Seal Water System | 30CF021 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | FALSE | FALSE | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA31CF021 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 line # S020GAC30-BR042-20-S9 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | FALSE
117 | Tauhara B Steamfield | Pump Station Seal Water System | 32CF030 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | FALSE | FALSE | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA32CF030 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 line # S020GAC30-BR051-20-S9 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | FALSE
118 | Tauhara B Steamfield | Pump Station Seal Water System | 32CF031 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | FALSE | FALSE | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA32CF031 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 line # S020GAC30-BR052-20-S9 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | FALSE
119 | Tauhara B Steamfield | Pump Station Seal Water System | 33CF040 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | FALSE | FALSE | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA33CF040 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 line # S020GAC30-BR061-20-S9 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  |  | 8.7 |  | 7 |  |  | FALSE
120 | Tauhara B Steamfield | Pump Station Seal Water System | 33CF041 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | FALSE | FALSE | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA33CF041 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 7.6 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 line # S020GAC30-BR062-20-S9 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  |  | 8.7 |  | 7 |  |  | FALSE
121 | Tauhara B Steamfield | Pump Station Seal Water System | 30CP501 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA30CP501 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GAC30-BR033-20-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
122 | Tauhara B Steamfield | Pump Station Seal Water System | 30CP502 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA30CP502 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GAC30-BR034-20-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
123 | Tauhara B Steamfield | Pump Station Seal Water System | 30CP503 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA30CP503 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GAC30-BR035-25-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
124 | Tauhara B Steamfield | Pump Station Seal Water System | 30CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 32 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020GWA30CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-43 | rev: 5.6 instment type: Temperature Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # S020GAC30-BR035-25-S9 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 50 | [5 empty] | FALSE
125 | Tauhara B Steamfield | Pump Station Seal Water System | 31CT020 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 32 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020GWA31CT020 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-43 | rev: 5.6 instment type: Temperature Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # S020GAC30-BR045-25-S9 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 50 | [5 empty] | FALSE
126 | Tauhara B Steamfield | Pump Station Seal Water System | 32CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 32 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020GWA32CT030 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-43 | rev: 5.6 instment type: Temperature Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # S020GAC30-BR055-25-S9 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 50 | [5 empty] | FALSE
127 | Tauhara B Steamfield | Pump Station Seal Water System | 33CT040 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 32 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020GWA33CT040 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-43 | rev: 5.6 instment type: Temperature Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # S020GAC30-BR065-25-S9 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 50 | [5 empty] | FALSE
128 | Tauhara B Steamfield | Pump Station Seal Water System | 31CP511 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA31CP511 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GAC30-BR043-20-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
129 | Tauhara B Steamfield | Pump Station Seal Water System | 31CP512 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA31CP512 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GAC30-BR044-20-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
130 | Tauhara B Steamfield | Pump Station Seal Water System | 31CP513 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA31CP513 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GAC30-BR045-25-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
131 | Tauhara B Steamfield | Pump Station Seal Water System | 32CP521 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA32CP521 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GAC30-BR053-20-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
132 | Tauhara B Steamfield | Pump Station Seal Water System | 32CP522 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA32CP522 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GAC30-BR054-20-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
133 | Tauhara B Steamfield | Pump Station Seal Water System | 32CP523 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA32CP523 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GAC30-BR055-25-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
134 | Tauhara B Steamfield | Pump Station Seal Water System | 33CP531 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA33CP531 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GAC30-BR063-20-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
135 | Tauhara B Steamfield | Pump Station Seal Water System | 33CP532 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA33CP532 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GAC30-BR064-20-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
136 | Tauhara B Steamfield | Pump Station Seal Water System | 33CP533 | - | Wika 72039876+14503369+ | - | FALSE | FALSE | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA33CP533 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GAC30-BR065-25-S9 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | FALSE
137 | Tauhara B Steamfield | Pump Station Seal Water System | 10CL010 | - | Vega PS21.XXXXXGMHB+GFL-PULS.GG | - | FALSE | FALSE |  | 0 to 3000 | Pump Station - Level | -edit- | 0 to 3000 | +/- 1% | TH00P020GWB10CL010 | CC-DAT-1468 | PO# 4500196238 | PRO-PID-56 | rev: 4.9 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 PRO-DAT-0078 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 750 | 1500 | 2250 | 3000 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
138 | Tauhara B Steamfield | Pump Station Seal Water System | 10CL011 | - | Vendor Supplied | - | FALSE | FALSE |  | 0 to 3000 | Pump Station - Level | -edit- | 0 to 3000 | +/- 1% | TH00P020GWB10CL011 |  | PO# Vendor Supplied | PRO-PID-56 | rev: 4.9 instment type: Level Indicator (Remote) make: Vendor Supplied Vendor: Vendor Supplied drwg: line # | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 750 | 1500 | 2250 | 3000 | 0 | 0 | 750 | 1500 | 2250 | 3000 | [9 empty] | FALSE
139 | Tauhara B Steamfield | Pump Station Seal Water System | 10CP510 | - | Rosemount 2051CD3A02A1BS5M4Q4+0305RC52B11B4 | - | FALSE | FALSE | 1.7 | 0 to 2.5 | Pump Station - Pressure | -edit- | 0 to 2.5 | +/- 1% | TH00P020GWB10CP510 | CCI-DAT-1462 | PO# 4500197800 | PRO-PID-56 | rev: 5.9 instment type: Pressure Differential Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0.625 | 1.25 | 1.875 | 2.5 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
140 | Tauhara B Steamfield | Pump Station Seal Water System | 21CF010 | - | SM6020, SMR12GGX50KG/US-100 | - | FALSE | FALSE |  | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWB21CF010 | CCI-DAT-1474 | PO# 4500196549 | PRO-PID-56 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: IFM Vendor: IFM drwg: CCI-DET-2707 line # | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
141 | Tauhara B Steamfield | Pump Station Seal Water System | 21CF020 | - | SM6020, SMR12GGX50KG/US-100 | - | FALSE | FALSE |  | 0 to 35 | Pump Station - Flow | -edit- | 0 to 35 | +/- 1% | TH00P020GWB21CF020 | CCI-DAT-1474 | PO# 4500196549 | PRO-PID-56 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: IFM Vendor: IFM drwg: CCI-DET-2707 line # | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 8.75 | 17.5 | 26.25 | 35 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
142 | Tauhara B Steamfield | Pump Station Seal Water System | 21CP511 | - | Wika 72039878+14298395 | - | FALSE | FALSE | 13 | 0 to 25 | Pump Station - Pressure | -edit- | 0 to 25 | +/- 1% | TH00P020GWB21CP511 | CCI-DAT-1460 | PO# 4500197977 | PRO-PID-56 | rev: 5.8 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | FALSE
143 | Tauhara B Steamfield | Pump Station Seal Water System | 21CP521 | - | Wika 72039878+14298395 | - | FALSE | FALSE | 13 | 0 to 25 | Pump Station - Pressure | -edit- | 0 to 25 | +/- 1% | TH00P020GWB21CP521 | CCI-DAT-1460 | PO# 4500197977 | PRO-PID-56 | rev: 5.8 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | FALSE
144 | Tauhara B Steamfield | Pump Station Seal Water System | 22CF010 | - | SM6020, SMR12GGX50KG/US-100 | - | FALSE | FALSE |  | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWB22CF010 | CCI-DAT-1474 | PO# 4500196549 | PRO-PID-56 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: IFM Vendor: IFM drwg: CCI-DET-2707 line # | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
145 | Tauhara B Steamfield | Pump Station Seal Water System | 22CF020 | - | SM6020, SMR12GGX50KG/US-100 | - | FALSE | FALSE |  | 0 to 35 | Pump Station - Flow | -edit- | 0 to 35 | +/- 1% | TH00P020GWB22CF020 | CCI-DAT-1474 | PO# 4500196549 | PRO-PID-56 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: IFM Vendor: IFM drwg: CCI-DET-2707 line # | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 8.75 | 17.5 | 26.25 | 35 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
146 | Tauhara B Steamfield | Pump Station Seal Water System | 22CP511 | - | Wika 72039878+14298395 | - | FALSE | FALSE | 13 | 0 to 25 | Pump Station - Pressure | -edit- | 0 to 25 | +/- 1% | TH00P020GWB22CP511 | CCI-DAT-1460 | PO# 4500197977 | PRO-PID-56 | rev: 5.8 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | FALSE
147 | Tauhara B Steamfield | Pump Station Seal Water System | 22CP521 | - | Wika 72039878+14298395 | - | FALSE | FALSE | 13 | 0 to 25 | Pump Station - Pressure | -edit- | 0 to 25 | +/- 1% | TH00P020GWB22CP521 | CCI-DAT-1460 | PO# 4500197977 | PRO-PID-56 | rev: 5.8 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 |  | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | FALSE
148 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 1120 | 0 to 1200 | Pump Station - Flow | -edit- | 0 to 1200 | +/- 1% | TH00P020LFC20CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-28 | rev: 5.6 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # P020LFC20-BR003-500-S11 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 300 | 600 | 900 | 1200 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
149 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL001 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | FALSE | FALSE |  | 0 to 10000 | Pump Station - Level | -edit- | 0 to 10000 | +/- 1% | TH00P020LFC20CL001 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-28 | rev: 3.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 STR-DET-0147 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2500 | 5000 | 7500 | 10000 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
150 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL002 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | FALSE | FALSE |  | 0 to 10000 | Pump Station - Level | -edit- | 0 to 10000 | +/- 1% | TH00P020LFC20CL002 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-28 | rev: 3.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 STR-DET-0147 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2500 | 5000 | 7500 | 10000 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
151 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL003 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | FALSE | FALSE |  | 0 to 10000 | Pump Station - Level | -edit- | 0 to 10000 | +/- 1% | TH00P020LFC20CL003 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-28 | rev: 3.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 STR-DET-0147 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2500 | 5000 | 7500 | 10000 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
152 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL010 | - | Vega B86.IXCMAXAGDHXATMKM | - | FALSE | FALSE | 0 | 0 to 6000 | Pump Station - Level | -edit- | 0 to 6000 | +/- 1% | TH00P020LFC20CL010 | CCI-DAT-1480 | PO# 4500189928 | PRO-PID-28 | rev: 3.2 instment type: Level Transmitter (Hydrostatic) make: Vega Vendor: Instrumatics drwg: GCV-DET-0179 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1500 | 3000 | 4500 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 200 | [5 empty] | FALSE
153 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL020 | - | Vega B86.IXCMAXAGDHXATMKM | - | FALSE | FALSE | 0 | 0 to 6000 | Pump Station - Level | -edit- | 0 to 6000 | +/- 1% | TH00P020LFC20CL020 | CCI-DAT-1480 | PO# 4500189928 | PRO-PID-28 | rev: 3.2 instment type: Level Transmitter (Hydrostatic) make: Vega Vendor: Instrumatics drwg: GCV-DET-0179 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1500 | 3000 | 4500 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 200 | [5 empty] | FALSE
154 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL030 | - | Vega B86.IXCMAXAGDHXATMKM | - | FALSE | FALSE | 0 | 0 to 6000 | Pump Station - Level | -edit- | 0 to 6000 | +/- 1% | TH00P020LFC20CL030 | CCI-DAT-1480 | PO# 4500189928 | PRO-PID-28 | rev: 3.2 instment type: Level Transmitter (Hydrostatic) make: Vega Vendor: Instrumatics drwg: GCV-DET-0179 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1500 | 3000 | 4500 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 200 | [5 empty] | FALSE
155 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL040 | - | Vega B86.IXCMAXAGDHXATMKM | - | FALSE | FALSE | 0 | 0 to 6000 | Pump Station - Level | -edit- | 0 to 6000 | +/- 1% | TH00P020LFC20CL040 | CCI-DAT-1480 | PO# 4500189928 | PRO-PID-28 | rev: 3.2 instment type: Level Transmitter (Hydrostatic) make: Vega Vendor: Instrumatics drwg: GCV-DET-0179 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1500 | 3000 | 4500 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 200 | [5 empty] | FALSE
156 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 16 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 25 | +/- 1% | TH00P020LFC20CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-28 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020LFC20-BR191-100-S11 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 3 | [5 empty] | FALSE
157 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT011 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 45 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020LFC20CT011 | CCI-DAT-1465 | PO# 45001918881 | PRO-PID-28 | rev: 6.3 instment type: Temperature Transmitter make: Rosemount Vendor: Custom Controls drwg: STR-DET-0147 line # | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 43 | 45 |  |  |  |  | FALSE
158 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT012 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT012 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
159 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT013 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT013 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
160 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT014 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT014 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
161 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT015 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT015 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
162 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT016 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT016 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
163 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT022 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT022 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
164 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT023 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT023 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
165 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT024 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT024 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
166 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT025 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT025 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
167 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT026 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT026 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
168 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY010 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020LFC20CY010 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
169 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY011 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020LFC20CY011 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
170 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY012 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Speed | -edit- | - | +/- 1% | TH00P020LFC20CY012 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Speed Indicator make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
171 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY020 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020LFC20CY020 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
172 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY021 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020LFC20CY021 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
173 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY022 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Speed | -edit- | - | +/- 1% | TH00P020LFC20CY022 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Speed Indicator make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
174 | Tauhara B Steamfield | Pump Station Condensate System | 10CF010 | - | Rosemount 8750WDMT2A2FNSA120CA1M4Q4Q8 | - | FALSE | FALSE | 455 | 0 to 10,000 | Pump Station - Flow | -edit- | 0 to 600 | +/- 1% | TH00P020NAB10CF010 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-28 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 line # P020NAB10-BR001-300-S11 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 150 | 300 | 450 | 600 | 0 | 4 | 8 | 12 | 16 | 20 | [6 empty] | 100 |  |  | FALSE
175 | Tauhara B Steamfield | Pump Station Condensate System | 10CP010 | - | Rosemount 2051CD3A02A1BS5M4Q4 | - | FALSE | FALSE | 0 | -2500 to 2500 | Pump Station - Pressure | -edit- | 0 to 250mbar | +/- 1% | TH00P020NAB10CP010 | CCI-DAT-1462 | PO# 4500191995 | PRO-PID-28 | rev: 3.2 instment type: Pressure Differential Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # P020NAB10-BR001-300-S11 | mbar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 200 | [5 empty] | FALSE
176 | Tauhara B Steamfield | Pump Station Condensate System | 10CP011 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 0.8 | -1 to 10.3 | Pump Station - Pressure | -edit- | 0 to 3 | +/- 1% | TH00P020NAB10CP011 | CCI-DAT-1461 | PO# 4500200505 | PRO-PID-28 | rev: 7.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020NAB10-BR001-300-S11 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0.75 | 1.5 | 2.25 | 3 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 0.4 |  |  |  | FALSE
177 | Tauhara B Steamfield | Pump Station Condensate System | 10CP012 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 3.5 | -1 to 10.3 | Pump Station - Pressure | -edit- | 0 to 10 | +/- 1% | TH00P020NAB10CP012 | CCI-DAT-1461 | PO# 4500200505 | PRO-PID-28 | rev: 7.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020NAB10-BR004-300-S11 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 9 |  | 6 |  |  |  | FALSE
178 | Tauhara B Steamfield | Pump Station Condensate System | 10CP030 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 3.5 | -1 to 10.3 | Pump Station - Pressure | -edit- | 0 to 10 | +/- 1% | TH00P020NAB10CP030 | CCI-DAT-1461 | PO# 4500200505 | PRO-PID-28 | rev: 7.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020NAB10-BR004-500-S11 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 9.9 | [5 empty] | FALSE
179 | Tauhara B Steamfield | Pump Station Condensate System | 10CT012 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NAB10CT012 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
180 | Tauhara B Steamfield | Pump Station Condensate System | 10CT013 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NAB10CT013 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
181 | Tauhara B Steamfield | Pump Station Condensate System | 10CT014 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NAB10CT014 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
182 | Tauhara B Steamfield | Pump Station Condensate System | 10CT015 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NAB10CT015 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
183 | Tauhara B Steamfield | Pump Station Condensate System | 10CT016 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NAB10CT016 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
184 | Tauhara B Steamfield | Pump Station Condensate System | 10CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 45 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020NAB10CT030 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-28 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # P020NAB10-BR004-500-S11 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 46 | [5 empty] | FALSE
185 | Tauhara B Steamfield | Pump Station Condensate System | 10CY010 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NAB10CY010 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
186 | Tauhara B Steamfield | Pump Station Condensate System | 10CY011 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NAB10CY011 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
187 | Tauhara B Steamfield | Pump Station Condensate System | 10CY012 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Speed | -edit- | - | +/- 1% | TH00P020NAB10CY012 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: instment type: Speed Indicator make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
188 | Tauhara B Steamfield | Pump Station Separated Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 1067 | 0 to 1264 tph 0 to 622.7 mb | Pump Station - Flow | -edit- | 0 to 1264 tph 0 to 622.7 mb | +/- 1% | TH00P020NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-26 | rev: 7.4 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # P020NDB10-BR031-400-CR1 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 316 | 632 | 948 | 1264 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
189 | Tauhara B Steamfield | Pump Station Separated Water System | 10CF020 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 1067 | 0 to 1264 tph 0 to 622.7 mb | Pump Station - Flow | -edit- | 0 to 1264 tph 0 to 622.7 mb | +/- 1% | TH00P020NDB10CF020 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-26 | rev: 7.4 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # P020NDB10-BR032-400-CR1 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 316 | 632 | 948 | 1264 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 40 | 20 |  |  | FALSE
190 | Tauhara B Steamfield | Pump Station Separated Water System | 10CF030 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 1067 | 0 to 1264 tph 0 to 622.7 mb | Pump Station - Flow | -edit- | 0 to 1264 tph 0 to 622.7 mb | +/- 1% | TH00P020NDB10CF030 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-26 | rev: 7.4 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # P020NDB10-BR033-400-CR1 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 316 | 632 | 948 | 1264 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 40 | 20 |  |  | FALSE
191 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP011 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP011 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020NDB10-BR021-400-CR1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 10 |  | 0.5 | 0.3 |  |  | FALSE
192 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP014 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP014 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020NDB10-BR031-400-CR1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
193 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP015 | - | Wika 72039917 (Model 733.14.100)++11585791 (Model 910.15) | - | FALSE | FALSE | 0 | 0 to 500 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP015 | CCI-DAT-1462 | PO# 4500189704 | PRO-PID-26 | rev: 3.2 instment type: Pressure Differential Indicator make: Wika Vendor: Wika drwg: CCI-DET-2702 line # P020NDB10-BR021-400-CR1 | mbar(g) | mbar | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 125 | 250 | 375 | 500 | 0 | 0 | 125 | 250 | 375 | 500 | [9 empty] | FALSE
194 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP021 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020NDB10-BR022-400-CR1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
195 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP024 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP024 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020NDB10-BR032-400-CR1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
196 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP025 | - | Wika 72039917 (Model 733.14.100)++11585791 (Model 910.15) | - | FALSE | FALSE | 0 | 0 to 500 | Pump Station - Pressure | -edit- | . | +/- 1% | TH00P020NDB10CP025 | CCI-DAT-1462 | PO# 4500189704 | PRO-PID-26 | rev: 3.2 instment type: Pressure Differential Indicator make: Wika Vendor: Wika drwg: CCI-DET-2702 line # P020NDB10-BR022-400-CR1 | mbar(g) | mbar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 125 | 250 | 375 | 500 | 0 | 0 | 125 | 250 | 375 | 500 | [9 empty] | FALSE
197 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP031 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP031 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020NDB10-BR023-400-CR1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 10 |  | 0.5 | 0.3 |  |  | FALSE
198 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP034 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP034 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020NDB10-BR033-400-CR1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
199 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP035 | - | Wika 72039917 (Model 733.14.100)++11585791 (Model 910.15) | - | FALSE | FALSE | 0 | 0 to 500 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP035 | CCI-DAT-1462 | PO# 4500189704 | PRO-PID-26 | rev: 3.2 instment type: Pressure Differential Indicator make: Wika Vendor: Wika drwg: CCI-DET-2702 line # P020NDB10-BR023-400-CR1 | mbar(g) | mbar | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 125 | 250 | 375 | 500 | 0 | 0 | 125 | 250 | 375 | 500 | [9 empty] | FALSE
200 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP040 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP040 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020NDB10-BR050-750-CR1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
201 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP512 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | 35 | See Notes | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP512 | PRO-DAT-0020 1460 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Pressure Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
202 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP513 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | 35 | See Notes | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP513 | PRO-DAT-0020 1460 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Pressure Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
203 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP522 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | 35 | See Notes | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP522 | PRO-DAT-0020 1460 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Pressure Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
204 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP523 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | 35 | See Notes | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP523 | PRO-DAT-0020 1460 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Pressure Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
205 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP532 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | 35 | See Notes | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP532 | PRO-DAT-0020 1460 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Pressure Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
206 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP533 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | 35 | See Notes | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP533 | PRO-DAT-0020 1460 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Pressure Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
207 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 123 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020NDB10CT010 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-26 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # P020NDB10-BR021-400-CR1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [5 empty] | 100 |  |  |  | FALSE
208 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT013 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT013 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
209 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT014 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT014 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
210 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT015 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT015 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
211 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT016 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT016 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
212 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT017 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT017 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
213 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT020 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 123 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020NDB10CT020 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-26 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # P020NDB10-BR022-400-CR1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [5 empty] | 100 |  |  |  | FALSE
214 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT023 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT023 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
215 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT024 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT024 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
216 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT025 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT025 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
217 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT026 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT026 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
218 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT027 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT027 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
219 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 120 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020NDB10CT030 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-26 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # P020NDB10-BR023-400-CR1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [5 empty] | 100 |  |  |  | FALSE
220 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT033 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT033 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
221 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT034 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT034 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
222 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT035 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT035 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
223 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT036 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT036 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
224 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT037 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT037 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Temperature Element make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | FALSE
225 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY010 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY010 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
226 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY011 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY011 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
227 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY012 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY012 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
228 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY013 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY013 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
229 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY014 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Speed | -edit- | - | +/- 1% | TH00P020NDB10CY014 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Speed Indicator make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
230 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY020 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY020 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
231 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY021 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY021 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
232 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY022 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY022 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
233 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY023 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY023 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
234 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY024 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Speed | -edit- | - | +/- 1% | TH00P020NDB10CY024 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Speed Indicator make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
235 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY030 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY030 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
236 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY031 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY031 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
237 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY032 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY032 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
238 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY033 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY033 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Vibration Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
239 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY034 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | Refer to Vendor | See Notes | Pump Station - Speed | -edit- | - | +/- 1% | TH00P020NDB10CY034 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: instment type: Speed Indicator make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied line # | mm/s | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
240 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CF010 | - | Rosemount 8705TSA020C1W0G1B3Q4Q8+8732EMT2A2M4+ | - | FALSE | FALSE | 707 | 0 to 720 | Pump Station - Flow | -edit- | 0 to 720 | +/- 1% | TH00P020PCB20CF010 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-44 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 line # S020PCB20-BR021-50-S8 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 180 | 360 | 540 | 720 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 500 |  |  |  | FALSE
241 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CF020 | - | Rosemount 8705TSA020C1W0G1B3Q4Q8+8732EMT2A2M4+ | - | FALSE | FALSE | 707 | 0 to 720 | Pump Station - Flow | -edit- | 0 to 720 | +/- 1% | TH00P020PCB20CF020 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-44 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 line # S020PCB20-BR022-50-S8 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 180 | 360 | 540 | 720 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 500 |  |  |  | FALSE
242 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP010 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 0.9 | -1 to 10.3 | Pump Station - Pressure | -edit- | 0 to 6 | +/- 1% | TH00P020PCB20CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-44 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020PCB20-BR001-80-S8 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.5 | 3 | 4.5 | 6 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
243 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP040 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 5.82 | -1 to 10.3 | Pump Station - Pressure | -edit- | 0 to 6 | +/- 1% | TH00P020PCB20CP040 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-44 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020PCB20-BR030-80-S8 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.5 | 3 | 4.5 | 6 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 5 |  | 3 | 0.5 |  |  | FALSE
244 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP510 | - | Wika 72039938 (Model 433.50.100)+14503369 (IV10)+ | - | FALSE | FALSE | 0.9 | 0 to 10 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020PCB20CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-44 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | [9 empty] | FALSE
245 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP520 | - | Wika 72039938 (Model 433.50.100)+14503369 (IV10)+ | - | FALSE | FALSE | 5.82 | 0 to 10 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020PCB20CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-44 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020PCB20-BR011-80-S8 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | [9 empty] | FALSE
246 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP530 | - | Wika 72039938 (Model 433.50.100)+14503369 (IV10)+ | - | FALSE | FALSE | 5.82 | 0 to 10 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020PCB20CP530 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-44 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020PCB20-BR012-80-S8 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | [9 empty] | FALSE
247 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 30 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB20CT010 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-46 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # P020PCB20-BR001-80-S8 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
248 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CT011 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 30 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB20CT011 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-46 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # P020PCB20-BR001-80-S8 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
249 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CT012 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 30 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB20CT012 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-46 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # P020PCB20-BR001-80-S8 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
250 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT011 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 40 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB22CT011 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-45 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # S020PCB22-BR051-50-S8 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 35 | [5 empty] | FALSE
251 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT012 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 40 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB22CT012 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-45 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # S020PCB22-BR052-50-S8 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 35 | [5 empty] | FALSE
252 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT013 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 40 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB22CT013 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-45 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # S020PCB22-BR053-50-S8 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 35 | [5 empty] | FALSE
253 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT021 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 30 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB22CT021 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-45 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 35 | [5 empty] | FALSE
254 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT022 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 30 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB22CT022 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-45 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 35 | [5 empty] | FALSE
255 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT023 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 30 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB22CT023 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-45 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 35 | [5 empty] | FALSE
256 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT031 | - | Rosemount 214CRWSMB1S4M0125SLAR1C2B1UAE065TBXW +114CM0050TAC2SC075AQ35Q5Q8XW | - | FALSE | FALSE | 30 | 0 to 250 | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020PCB22CT031 | CCI-DAT-1466 | PO# 4500197800 | PRO-PID-45 | rev: 5.9 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 |  | 1 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
257 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT032 | - | Rosemount 214CRWSMB1S4M0125SLAR1C2B1UAE065TBXW +114CM0050TAC2SC075AQ35Q5Q8XW | - | FALSE | FALSE | 30 | 0 to 250 | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020PCB22CT032 | CCI-DAT-1466 | PO# 4500197800 | PRO-PID-45 | rev: 5.9 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 |  | 2 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
258 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT033 | - | Rosemount 214CRWSMB1S4M0125SLAR1C2B1UAE065TBXW +114CM0050TAC2SC075AQ35Q5Q8XW | - | FALSE | FALSE | 30 | 0 to 250 | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020PCB22CT033 | CCI-DAT-1466 | PO# 4500197800 | PRO-PID-45 | rev: 5.9 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 |  | 3 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
259 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 12 | +/- 1% | TH00P020QFB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-47 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020QFB10-BR013-50-OFFSPEC | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3 | 6 | 9 | 12 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 10 |  |  |  | FALSE
260 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP020 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 12 | +/- 1% | TH00P020QFB10CP020 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-47 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020QFB10-BR023-50-OFFSPEC | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3 | 6 | 9 | 12 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 10 |  |  |  | FALSE
261 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP030 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 12 | +/- 1% | TH00P020QFB10CP030 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-47 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020QFB10-BR033-50-OFFSPEC | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3 | 6 | 9 | 12 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 10 |  |  |  | FALSE
262 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP040 | - | Rosemount 3051TG3A2B21BB4M4T1Q4Q8S5 | - | FALSE | FALSE | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 12 | +/- 1% | TH00P020QFB10CP040 | CCI-DAT-1461 | PO# 4500193144 | PRO-PID-47 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020QFB10-BR043-50-OFFSPEC | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3 | 6 | 9 | 12 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 10 |  |  |  | FALSE
263 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP050 | - | Rosemount 3051TG3A2B21BB4M4T1Q4Q8S5 | - | FALSE | FALSE | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 12 | +/- 1% | TH00P020QFB10CP050 | CCI-DAT-1461 | PO# 4500193144 | PRO-PID-47 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020QFB10-BR053-50-OFFSPEC | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3 | 6 | 9 | 12 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 10 |  |  |  | FALSE
264 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP511 | - | Wika 72039879 + 14298395 | - | FALSE | FALSE | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 16 | +/- 1% | TH00P020QFB10CP511 | CCI-DAT-1460 | PO# 4500196708 | PRO-PID-47 | rev: 6.3 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # P020QFB10-BR013-50-S6 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4 | 8 | 12 | 16 |  | 0 | 4 | 8 | 12 | 16 | [9 empty] | FALSE
265 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP521 | - | Wika 72039879 + 14298395 | - | FALSE | FALSE | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 16 | +/- 1% | TH00P020QFB10CP521 | CCI-DAT-1460 | PO# 4500196708 | PRO-PID-47 | rev: 6.3 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # P020QFB10-BR023-50-S6 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4 | 8 | 12 | 16 |  | 0 | 4 | 8 | 12 | 16 | [9 empty] | FALSE
266 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP531 | - | Wika 72039879 + 14298395 | - | FALSE | FALSE | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 16 | +/- 1% | TH00P020QFB10CP531 | CCI-DAT-1460 | PO# 4500196708 | PRO-PID-47 | rev: 6.3 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # P020QFB10-BR033-50-S6 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4 | 8 | 12 | 16 |  | 0 | 4 | 8 | 12 | 16 | [9 empty] | FALSE
267 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP541 | - | Wika 72039879 + 14298395 | - | FALSE | FALSE | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 16 | +/- 1% | TH00P020QFB10CP541 | CCI-DAT-1460 | PO# 4500196708 | PRO-PID-47 | rev: 6.3 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # P020QFB10-BR033-50-S6 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4 | 8 | 12 | 16 |  | 0 | 4 | 8 | 12 | 16 | [9 empty] | FALSE
268 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP551 | - | Wika 72039879 + 14298395 | - | FALSE | FALSE | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 16 | +/- 1% | TH00P020QFB10CP551 | CCI-DAT-1460 | PO# 4500196708 | PRO-PID-47 | rev: 6.3 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # P020QFB10-BR033-50-S6 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4 | 8 | 12 | 16 |  | 0 | 4 | 8 | 12 | 16 | [9 empty] | FALSE
269 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP523 | - | Wika 72039879 + 14298395 | - | FALSE | FALSE | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 16 | +/- 1% | TH00P020QFB10CP523 | CCI-DAT-1460 | PO# 4500196708 | PRO-PID-47 | rev: 6.3 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # P020QFB10-BR033-50-S6 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4 | 8 | 12 | 16 |  | 0 | 4 | 8 | 12 | 16 | [9 empty] | FALSE
270 | Tauhara B Steamfield | Separation Plant Raw Water System | 10CL010 | - | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8 | - | FALSE | FALSE |  | See notes | Separation Plant - Level | -edit- | TBC | +/- 1% | TH00S020GAC10CL010 | CCI-DAT-1468 | PO# 4500191995 | PRO-PID-51 | rev: 3.2 instment type: Level Transmitter (Radar) make: Rosemount Vendor: Custom Controls drwg: Nozzle Mount PRO-DAT-0088 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
271 | Tauhara B Steamfield | Separation Plant Raw Water System | 10CL011 | - | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8 | - | FALSE | FALSE |  | See notes | Separation Plant - Level | -edit- | TBC | +/- 1% | TH00S020GAC10CL011 | CCI-DAT-1468 | PO# 4500191995 | PRO-PID-51 | rev: 3.2 instment type: Level Transmitter (Radar) make: Rosemount Vendor: Custom Controls drwg: Nozzle Mount PRO-DAT-0088 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
272 | Tauhara B Steamfield | Separation Plant Raw Water System | 10CL020 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | Refer to Notes | +/- 1% | TH00S020GAC10CL020 | CCI-DAT-1471 PRO-DAT-0088 | PO# Vendor Supplied | PRO-PID-51 | rev: instment type: Level Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2705 line # | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
273 | Tauhara B Steamfield | Separation Plant Raw Water System | 10CL021 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | Refer to Notes | +/- 1% | TH00S020GAC10CL021 | CCI-DAT-1471 PRO-DAT-0088 | PO# Vendor Supplied | PRO-PID-51 | rev: instment type: Level Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2705 line # | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
274 | Tauhara B Steamfield | Separation Plant Raw Water System | 10CP001 | - | Rosemount 2051CD4A02A1BS5M4Q4 | - | FALSE | FALSE | 3.49 | 0 to 20 | Separation Plant - Pressure | -edit- | 0 to 4 | +/- 1% | TH00S020GAC10CP001 | CCI-DAT-1462 | PO# 4500191995 | PRO-PID-51 | rev: 3.2 instment type: Pressure Differential Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # S020GAC10-BR013-50-S8 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1 | 2 | 3 | 4 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 2 | [5 empty] | FALSE
275 | Tauhara B Steamfield | Separation Plant Raw Water System | 10CP002 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 2.98 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020GAC10CP002 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-51 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020GAC10-BR001-50-S8 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
276 | Tauhara B Steamfield | Separation Plant Raw Water System | 21CP020 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 2.98 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 8 | +/- 1% | TH00S020GAC21CP020 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-51 | rev: 6.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # P020GAC21-BR050-50-S8 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2 | 4 | 6 | 8 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 4 |  | 1 |  |  |  | FALSE
277 | Tauhara B Steamfield | Separation Plant Raw Water System | 22CF501 | - | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - | FALSE | FALSE | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | - | +/- 1% | TH00S020GAC22CF501 | QCM-PRO-SPC-0109 | PO# 4500193000 | PRO-PID-101 | rev: 3.5 instment type: Flow Indicator make: Brooks Vendor: Wika drwg: Vendor Designed line # S020GAC22-BR061-25-S8 | l/m | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
278 | Tauhara B Steamfield | Separation Plant Raw Water System | 22CF510 | - | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - | FALSE | FALSE | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | - | +/- 1% | TH00S020GAC22CF510 | QCM-PRO-SPC-0109 | PO# 4500193000 | PRO-PID-101 | rev: 3.5 instment type: Flow Indicator make: Brooks Vendor: Wika drwg: Vendor Designed line # S020GAC22-BR062-25-S8 | l/m | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
279 | Tauhara B Steamfield | Separation Plant Raw Water System | 22CF520 | - | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - | FALSE | FALSE | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | - | +/- 1% | TH00S020GAC22CF520 | QCM-PRO-SPC-0109 | PO# 4500193000 | PRO-PID-100 | rev: 3.5 instment type: Flow Indicator make: Brooks Vendor: Wika drwg: Vendor Designed line # S020GAC22-BR081-25-S8 | l/m | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
280 | Tauhara B Steamfield | Separation Plant Raw Water System | 22CF530 | - | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - | FALSE | FALSE | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | - | +/- 1% | TH00S020GAC22CF530 | QCM-PRO-SPC-0109 | PO# 4500193000 | PRO-PID-100 | rev: 3.5 instment type: Flow Indicator make: Brooks Vendor: Wika drwg: Vendor Designed line # S020GAC22-BR082-25-S8 | l/m | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
281 | Tauhara B Steamfield | Separation Plant Raw Water System | 22CF540 | - | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - | FALSE | FALSE | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | - | +/- 1% | TH00S020GAC22CF540 | QCM-PRO-SPC-0109 | PO# 4500193000 | PRO-PID-100 | rev: 3.5 instment type: Flow Indicator make: Brooks Vendor: Wika drwg: Vendor Designed line # S020GAC22-BR083-25-S8 | l/m | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
282 | Tauhara B Steamfield | Separation Plant Raw Water System | 22CF550 | - | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - | FALSE | FALSE | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | - | +/- 1% | TH00S020GAC22CF550 | QCM-PRO-SPC-0109 | PO# 4500193000 | PRO-PID-100 | rev: 3.5 instment type: Flow Indicator make: Brooks Vendor: Wika drwg: Vendor Designed line # S020GAC22-BR084-25-S8 | l/m | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
283 | Tauhara B Steamfield | Separation Plant Calcite Inhibitor Tank | 10CL010 | - | Vega PS21.XXXXXGMHB+GFL-PLUS.GG | - | FALSE | FALSE |  | 0 to 2500 | Separation Plant - Level | -edit- | 0 to 2500 | +/- 1% | TH00S020GBK10CL010 | CCI-DAT-1468 | PO# 4500193055 4500195517 | PRO-PID-53 | rev: 4.7 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 625 | 1250 | 1875 | 2500 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
284 | Tauhara B Steamfield | Separation Plant Calcite Inhibitor Sump | 10CL011 | - | Vega PS21.XXXXXGMHB+MBA.BB | - | FALSE | FALSE |  | 0 to 1000 | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020GBK10CL011 | CCI-DAT-1468 | PO# 4500193055 | PRO-PID-53 | rev: 7.7 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 250 | 500 | 750 | 1000 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
285 | Tauhara B Steamfield | Separation Plant Calcite Inhibitor Tank | 10CL020 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE |  | 0 to 2500 | Separation Plant - Level | -edit- | 0 to 2500 | +/- 1% | TH00S020GBK10CL020 | CCI-DAT-1471 | PO# Vendor Supplied | PRO-PID-53 | rev: 2.2 instment type: Level Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2706 line # | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 625 | 1250 | 1875 | 2500 | 0 | 0 | 625 | 1250 | 1875 | 2500 | [9 empty] | FALSE
286 | Tauhara B Steamfield | Separation Plant Potable Water System | 10CL010 | - | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8 | - | FALSE | FALSE |  | See notes | Separation Plant - Level | -edit- | TBC | +/- 1% | TH00S020GKA10CL010 | CCI-DAT-1468 | PO# 4500191995 | PRO-PID-40 | rev: 3.2 instment type: Level Transmitter (Radar) make: Rosemount Vendor: Custom Controls drwg: Nozzle Mount PRO-DAT-0074 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
287 | Tauhara B Steamfield | Separation Plant Potable Water System | 10CL011 | - | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8 | - | FALSE | FALSE |  | See notes | Separation Plant - Level | -edit- | TBC | +/- 1% | TH00S020GKA10CL011 | CCI-DAT-1468 | PO# 4500191995 | PRO-PID-40 | rev: 3.2 instment type: Level Transmitter (Radar) make: Rosemount Vendor: Custom Controls drwg: Nozzle Mount PRO-DAT-0074 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
288 | Tauhara B Steamfield | Separation Plant Potable Water System | 10CL020 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | Refer to Notes | +/- 1% | TH00S020GKA10CL020 | CCI-DAT-1471 PRO-DAT-0074 | PO# Vendor Supplied | PRO-PID-40 | rev: instment type: Level Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2705 line # | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
289 | Tauhara B Steamfield | Separation Plant Potable Water System | 10CL021 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | Refer to Notes | +/- 1% | TH00S020GKA10CL021 | CCI-DAT-1471 PRO-DAT-0074 | PO# Vendor Supplied | PRO-PID-40 | rev: instment type: Level Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2705 line # | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
290 | Tauhara B Steamfield | Separation Plant Potable Water System | 21CF191 | - | Wika 72039911++ (FSD-4 Model) | - | FALSE | FALSE | >1.5 | 0 to 2 | Separation Plant - Flow | -edit- |  | +/- 1% | TH00S020GKA21CF191 | CCI-DAT-1476 | PO# 4500189704 | PRO-PID-40 | rev: 6.1 instment type: Flow Switch make: Wika Vendor: Wika drwg: CCI-DET-2709 line # S020GKA20-BR051-50-S8 | kg/s | kg/s | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0.5 | 1 | 1.5 | 2 | 0 | 0 | 0.5 | 1 | 1.5 | 2 | [9 empty] | FALSE
291 | Tauhara B Steamfield | Separation Plant Potable Water System | 21CF192 | - | Wika 72039911++ (FSD-4 Model) | - | FALSE | FALSE | >1.5 | 0 to 2 | Separation Plant - Flow | -edit- |  | +/- 1% | TH00S020GKA21CF192 | CCI-DAT-1476 | PO# 4500189704 | PRO-PID-40 | rev: 6.1 instment type: Flow Switch make: Wika Vendor: Wika drwg: CCI-DET-2709 line # S020GKA20-BR051-50-S8 | kg/s | kg/s | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0.5 | 1 | 1.5 | 2 | 0 | 0 | 0.5 | 1 | 1.5 | 2 | [9 empty] | FALSE
292 | Tauhara B Steamfield | Separation Plant Potable Water System | 21CF193 | - | Wika 72039911++ (FSD-4 Model) | - | FALSE | FALSE | >1.5 | 0 to 2 | Separation Plant - Flow | -edit- |  | +/- 1% | TH00S020GKA21CF193 | CCI-DAT-1476 | PO# 4500189704 | PRO-PID-40 | rev: 6.1 instment type: Flow Switch make: Wika Vendor: Wika drwg: CCI-DET-2709 line # S020GKA20-BR051-50-S8 | kg/s | kg/s | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0.5 | 1 | 1.5 | 2 | 0 | 0 | 0.5 | 1 | 1.5 | 2 | [9 empty] | FALSE
293 | Tauhara B Steamfield | Separation Plant Potable Water System | 21CF194 | - | Wika 72039911++ (FSD-4 Model) | - | FALSE | FALSE | >1.5 | 0 to 4 | Separation Plant - Flow | -edit- |  | +/- 1% | TH00S020GKA21CF194 | CCI-DAT-1476 | PO# 4500189704 | PRO-PID-40 | rev: 6.1 instment type: Flow Switch make: Wika Vendor: Wika drwg: CCI-DET-2709 line # S020GKA20-BR052-50-S8 | kg/s | kg/s | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1 | 2 | 3 | 4 | 0 | 0 | 1 | 2 | 3 | 4 | [9 empty] | FALSE
294 | Tauhara B Steamfield | Pump Station Potable Water System | 21CF195 | - | Wika 72039911++ (FSD-4 Model) | - | FALSE | FALSE | >1.5 | 0 to 3 | Pump Station - Flow | -edit- |  | +/- 1% | TH00S020GKA21CF195 | CCI-DAT-1476 | PO# 4500189704 | PRO-PID-40 | rev: 6.1 instment type: Flow Switch make: Wika Vendor: Wika drwg: CCI-DET-2709 line # S020GKA20-BR053-50-S8 | kg/s | kg/s | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0.75 | 1.5 | 2.25 | 3 |  | 0 | 0.75 | 1.5 | 2.25 | 3 | [9 empty] | FALSE
295 | Tauhara B Steamfield | Pump Station Potable Water System | 21CF196 | - | Wika 72039911++ (FSD-4 Model) | - | FALSE | FALSE | >1.5 | 0 to 3 | Pump Station - Flow | -edit- |  | +/- 1% | TH00S020GKA21CF196 | CCI-DAT-1476 | PO# 4500200070 | PRO-PID-40 | rev: 7.3 instment type: Flow Switch make: Wika Vendor: Wika drwg: CCI-DET-2709 line # S020GKA20-BR053-50-S8 | kg/s | kg/s | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0.75 | 1.5 | 2.25 | 3 |  | 0 | 0.75 | 1.5 | 2.25 | 3 | [9 empty] | FALSE
296 | Tauhara B Steamfield | Separation Plant Potable Water System | 20CP520 | - | Wika 72039882 (Model 433.50)+14503369+ (Model IV10) | - | FALSE | FALSE | 3.14 | 0 to 25 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020GKA20CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-40 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020GKA20-BR043-50-S8 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | FALSE
297 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 11CF010 | - | Vendor Supplied | - | FALSE | FALSE | - | - | Separation Plant - Flow | -edit- | 0 | +/- 1% | TH00S020GWA11CF010 |  | PO# Vendor Supplied | PRO-PID-55 | rev: 4.9 instment type: Flow Transmitter (Magnetic) make: Vendor Supplied Vendor: Vendor Supplied drwg: line # | 0 | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
298 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 11CF020 | - | Vendor Supplied | - | FALSE | FALSE | - | - | Separation Plant - Flow | -edit- | 0 | +/- 1% | TH00S020GWA11CF020 |  | PO# Vendor Supplied | PRO-PID-55 | rev: 4.9 instment type: Flow Transmitter (Magnetic) make: Vendor Supplied Vendor: Vendor Supplied drwg: line # | 0 | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
299 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CL310 | - | Vega P21.XXXXXABMIB | - | FALSE | FALSE | - | - | Separation Plant - Level | -edit- | 0 | +/- 1% | TH00S020GWA10CL310 |  | PO# 4500196706 | PRO-PID-55 | rev: 4.9 instment type: Level Switch make: Vega Vendor: Instrumatics drwg: line # | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | FALSE
300 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 12CT010 | - | Rosemount 644HANAJ5M5Q4+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAA2SC075AQ35Q5Q8XW | - | FALSE | FALSE | 123 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020GWA12CT010 | CCI-DAT-1465 | PO# Vendor Supplied | PRO-PID-55 | rev: 4.9 instment type: Temperature Indicating Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: line # | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
301 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CT010 | - | Rosemount 644HANAJ5M5Q4 | - | FALSE | FALSE | 123 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020GWA10CT010 | CCI-DAT-1465 | PO# 4500200505 | PRO-PID-55 | rev: 7.4 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
302 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CT020 | - | Rosemount 644HANAJ5M5Q4+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAA2SC075AQ35Q5Q8XW | - | FALSE | FALSE | 123 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020GWA10CT020 | CCI-DAT-1465 | PO# 4500200505 | PRO-PID-55 | rev: 7.4 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 line # | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
303 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CT010Temp | - | Servotech QT21GS2+QR08N+HKNPB | - | FALSE | FALSE | 123 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020GWA10CT010Temp | CCI-DAT-1465 | PO# 4500200319 | PRO-PID-55 | rev: 6.5 instment type: Temperature Indicating Transmitter make: Servotech Vendor: Servotech drwg: CCI-DET-2703 line # | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
304 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CT020Temp | - | Servotech QT21GS2+QR08N+HKNPB | - | FALSE | FALSE | 123 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020GWA10CT020Temp | CCI-DAT-1465 | PO# 4500200319 | PRO-PID-55 | rev: 6.5 instment type: Temperature Indicating Transmitter make: Servotech Vendor: Servotech drwg: CCI-DET-2703 line # | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
305 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 11CP510 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE | - | See notes | Separation Plant - Pressure | -edit- | 0 | +/- 1% | TH00S020GWA11CP510 |  | PO# Vendor Supplied | PRO-PID-55 | rev: 4.9 instment type: Pressure Differential Transmitter make: Vendor Supplied Vendor: Vendor Supplied drwg: line # | - | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | FALSE
306 | Tauhara B Steamfield | Separation Plant Process Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 7.6 | 0 to 18 | Separation Plant - Flow | -edit- | 0 to 18 | +/- 1% | TH00S020LCE10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-18 | rev: 6.3 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # S020LCE10-BR010-40-S4 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4.5 | 9 | 13.5 | 18 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 5.7 |  |  |  | FALSE
307 | Tauhara B Steamfield | Separation Plant Process Water System | 10CF020 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 2.2 | 0 to 7.2 | Separation Plant - Flow | -edit- | 0 to 7.2 | +/- 1% | TH00S020LCE10CF020 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-20 | rev: 5.6 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # S020LCE10-BR020-40-S4 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.8 | 3.6 | 5.4 | 7.2 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 |  | 20 | L/min |  |  | FALSE
308 | Tauhara B Steamfield | Separation Plant Process Water System | 10CF030 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 1.8 | 0 to 7.2 | Separation Plant - Flow | -edit- | 0 to 7.2 | +/- 1% | TH00S020LCE10CF030 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-22 | rev: 5.6 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # S020LCE10-BR030-40-S4 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.8 | 3.6 | 5.4 | 7.2 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 |  | 20 | L/min |  |  | FALSE
309 | Tauhara B Steamfield | Separation Plant Process Water System | 10CF040 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 1.8 | 0 to 7.2 | Separation Plant - Flow | -edit- | 0 to 7.2 | +/- 1% | TH00S020LCE10CF040 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-24 | rev: 5.6 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # S020LCE10-BR040-40-S4 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.8 | 3.6 | 5.4 | 7.2 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 |  | 20 | L/min |  |  | FALSE
310 | Tauhara B Steamfield | Separation Plant Process Water System | 10CP510 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 16.72 | 0 to 60 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020LCE10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-18 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020LCE10-BR010-40-S4 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
311 | Tauhara B Steamfield | Separation Plant Process Water System | 10CP520 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 8.78 | 0 to 60 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020LCE10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-20 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020LCE10-BR020-40-S4 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
312 | Tauhara B Steamfield | Separation Plant Process Water System | 10CP530 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 1.16 | 0 to 60 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020LCE10CP530 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-22 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020LCE10-BR030-40-S4 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
313 | Tauhara B Steamfield | Separation Plant Process Water System | 10CP540 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 1.16 | 0 to 60 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020LCE10CP540 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-24 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020LCE10-BR040-40-S4 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
314 | Tauhara B Steamfield | Separation Plant Deoxygenated Tank 1 | 20CL010 | - | Vega PS21.XXXXXGMHB+GFL-PLUS.GG | - | FALSE | FALSE |  | 0 to 3125 | Separation Plant - Level | -edit- | 0 to 3125 | +/- 1% | TH00S020LCE20CL010 | CCI-DAT-1468 | PO# 4500193055 | PRO-PID-53 | rev: 5.6 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 781.25 | 1562.5 | 2343.75 | 3125 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
315 | Tauhara B Steamfield | Separation Plant Deoxygenated Tank 2 | 20CL011 | - | Vega PS21.XXXXXGMHB+GFL-PLUS.GG | - | FALSE | FALSE |  | 0 to 3125 | Separation Plant - Level | -edit- | 0 to 3125 | +/- 1% | TH00S020LCE20CL011 | CCI-DAT-1468 | PO# 4500193055 | PRO-PID-53 | rev: 5.6 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 781.25 | 1562.5 | 2343.75 | 3125 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
316 | Tauhara B Steamfield | Separation Plant Deoxygenated Tank 1 | 20CL020 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE |  | 0 to 3125 | Separation Plant - Level | -edit- | 0 to 3125 | +/- 1% | TH00S020LCE20CL020 | CCI-DAT-1471 | PO# Vendor Supplied | PRO-PID-53 | rev: 2.2 instment type: Level Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2706 line # | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 781.25 | 1562.5 | 2343.75 | 3125 | 0 | 0 | 781.25 | 1562.5 | 2343.75 | 3125 | [9 empty] | FALSE
317 | Tauhara B Steamfield | Separation Plant Deoxygenated Tank 2 | 20CL021 | - | Vendor Supplied Vendor Supplied | - | FALSE | FALSE |  | 0 to 3125 | Separation Plant - Level | -edit- | 0 to 3125 | +/- 1% | TH00S020LCE20CL021 | CCI-DAT-1471 | PO# Vendor Supplied | PRO-PID-53 | rev: 2.2 instment type: Level Gauge make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2706 line # | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 781.25 | 1562.5 | 2343.75 | 3125 | 0 | 0 | 781.25 | 1562.5 | 2343.75 | 3125 | [9 empty] | FALSE
318 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT001 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L050NDA10CT001 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR501-500-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
319 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT002 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L050NDA10CT002 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR511-500-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
320 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT003 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L050NDA10CT003 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR521-500-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
321 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT011 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L060NDA10CT011 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR502-500-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
322 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT012 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L060NDA10CT012 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR512-500-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
323 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT013 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L060NDA10CT013 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR522-500-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
324 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT021 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L070NDA10CT021 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR503-500-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
325 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT022 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L070NDA10CT022 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR513-500-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
326 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT023 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L070NDA10CT023 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR523-500-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
327 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT041 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 215 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA10CT041 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-18 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR541-500-CH3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
328 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT042 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 215 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA10CT042 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-18 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR542-500-CH3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
329 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT043 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 215 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA10CT043 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-18 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR543-500-CH3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
330 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT044 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 215 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA10CT044 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-18 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR544-500-CH3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
331 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT045 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 215 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA10CT045 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-18 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR545-500-CH3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
332 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT046 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 215 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA10CT046 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-18 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR546-500-CH3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
333 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT051 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 188 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA20CT051 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-20 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR551-500-CI3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
334 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT052 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 188 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA20CT052 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-20 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR552-500-CI3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
335 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT053 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 188 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA20CT053 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-20 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR553-500-CI3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
336 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT054 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 188 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA20CT054 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-20 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR554-500-CI3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
337 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT061 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA31CT061 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-22 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR561-500-CL3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
338 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT062 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA31CT062 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-22 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR562-500-CL3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
339 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT063 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA31CT063 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-22 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR563-500-CL3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
340 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT064 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA31CT064 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-22 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR564-500-CL3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
341 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT065 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA31CT065 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-22 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR565-500-CL3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
342 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT066 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA31CT066 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-22 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR566-500-CL3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
343 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT071 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA32CT071 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-24 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR571-500-CL3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
344 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT072 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA32CT072 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-24 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR572-500-CL3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
345 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT073 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA32CT073 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-24 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR573-500-CL3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
346 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT074 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA32CT074 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-24 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR574-500-CL3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
347 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT075 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA32CT075 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-24 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR575-500-CL3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
348 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT076 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA32CT076 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-24 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020LFC10-BR576-500-CL3 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | FALSE
349 | Tauhara B Steamfield | Separation Plant Steam System | 10CF010 | - | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0 | - | FALSE | FALSE | 740 | 0 to 900 | Separation Plant - Flow | -edit- | 0 to 900 | +/- 1% | TH00S020NAA10CF010 | CCI-DAT-1478 | PO# 4500191995 | PRO-PID-18 | rev: 5.6 instment type: Flow Transmitter (Vortex) make: InnovaMass Vendor: Custom Controls drwg: MEC-DET-1045 line # S020NAA10-BR010-1200-CH2 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 225 | 450 | 675 | 900 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
350 | Tauhara B Steamfield | Separation Plant Steam System | 10CL410 | - | Bliss Anand R/36/M/S/2/1/B/N/N/X/PN/S/772MM | - | FALSE | FALSE | - | - | Separation Plant - Level | -edit- | 0 to 800 | +/- 1% | TH00S020NAA10CL410 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-18 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type HP08 line # S020NAA10-BR410-900-CH2 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 200 | 400 | 600 | 800 | 0 | 0 | 200 | 400 | 600 | 800 | [9 empty] | FALSE
351 | Tauhara B Steamfield | Separation Plant Steam System | 10CL450 | - | Bliss Anand R/47/M/S/2/1/B/N/N/X/PN/S/1156MM | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | 0 to 1200 | +/- 1% | TH00S020NAA10CL450 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-19 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type HP12 line # S020NAA10-BR450-900-CH2 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 300 | 600 | 900 | 1200 | 0 | 0 | 300 | 600 | 900 | 1200 | [9 empty] | FALSE
352 | Tauhara B Steamfield | Separation Plant Steam System | 10CL451 | - | Rosemount 5301HA2P1N4AM00120ABNAM1Q4Q8QTDA1S2 | - | FALSE | FALSE |  | 0 to 1200 | Separation Plant - Level | -edit- | 0 to 1200 | +/- 1% | TH00S020NAA10CL451 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-19 | rev: 3.2 instment type: Level Transmitter (GW Radar) make: Rosemount Vendor: Custom Controls drwg: 000-MEC-DET-1231 line # S020NAA10-BR450-900-CH2 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 300 | 600 | 900 | 1200 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 1100 |  | 100 |  |  |  | FALSE
353 | Tauhara B Steamfield | Separation Plant Steam System | 10CL460 | - | Bliss Anand R/36/M/S/2/1/B/N/N/X/PN/S/772MM | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | 0 to 800 | +/- 1% | TH00S020NAA10CL460 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-19 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type HP08 line # S020NAA10-BR460-900-CH2 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 200 | 400 | 600 | 800 | 0 | 0 | 200 | 400 | 600 | 800 | [9 empty] | FALSE
354 | Tauhara B Steamfield | Separation Plant Steam System | 10CP021 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NAA10CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA10-BR010-1050-CH2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
355 | Tauhara B Steamfield | Separation Plant Steam System | 10CP022 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NAA10CP022 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA10-BR010-1050-CH2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
356 | Tauhara B Steamfield | Separation Plant Steam System | 10CP023 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NAA10CP023 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA10-BR010-1050-CH2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
357 | Tauhara B Steamfield | Separation Plant Steam System | 10CP031 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - | FALSE | FALSE | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NAA10CP031 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA10-BR010-1050-CH2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
358 | Tauhara B Steamfield | Separation Plant Steam System | 10CP032 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - | FALSE | FALSE | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NAA10CP032 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA10-BR010-1050-CH2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
359 | Tauhara B Steamfield | Separation Plant Steam System | 10CP033 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - | FALSE | FALSE | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NAA10CP033 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA10-BR010-1050-CH2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
360 | Tauhara B Steamfield | Separation Plant Steam System | 11CF452 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 8.7 | 0 to 20 | Separation Plant - Flow | -edit- | 0 to 18 | +/- 1% | TH00S020NAA11CF452 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-19 | rev: 5.6 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # S020NAA11-BR451-100-CH2 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4.5 | 9 | 13.5 | 18 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 250 |  | 20 |  |  |  | FALSE
361 | Tauhara B Steamfield | Separation Plant Steam System | 20CF010 | - | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0 | - | FALSE | FALSE | 191 | 0 to 216 | Separation Plant - Flow | -edit- | 0 to 216 | +/- 1% | TH00S020NAA20CF010 | CCI-DAT-1478 | PO# 4500191995 | PRO-PID-21 | rev: 5.6 instment type: Flow Transmitter (Vortex) make: InnovaMass Vendor: Custom Controls drwg: MEC-DET-1045 line # S020NAA20-BR010-750-CI2 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 54 | 108 | 162 | 216 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
362 | Tauhara B Steamfield | Separation Plant Steam System | 20CL410 | - | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | 0 to 600 | +/- 1% | TH00S020NAA20CL410 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-20 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type IP06 line # S020NAA20-BR410-600-CI2 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 150 | 300 | 450 | 600 | 0 | 0 | 150 | 300 | 450 | 600 | [9 empty] | FALSE
363 | Tauhara B Steamfield | Separation Plant Steam System | 20CL450 | - | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | 0 to 600 | +/- 1% | TH00S020NAA20CL450 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-21 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type IP06 line # S020NAA20-BR450-600-CI2 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 150 | 300 | 450 | 600 | 0 | 0 | 150 | 300 | 450 | 600 | [9 empty] | FALSE
364 | Tauhara B Steamfield | Separation Plant Steam System | 20CL460 | - | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | 0 to 600 | +/- 1% | TH00S020NAA20CL460 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-21 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type IP06 line # S020NAA20-BR460-600-CI2 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 150 | 300 | 450 | 600 | 0 | 0 | 150 | 300 | 450 | 600 | [9 empty] | FALSE
365 | Tauhara B Steamfield | Separation Plant Steam System | 20CP021 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 15 | +/- 1% | TH00S020NAA20CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-20 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA20-BR010-750-CI2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
366 | Tauhara B Steamfield | Separation Plant Steam System | 20CP022 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 15 | +/- 1% | TH00S020NAA20CP022 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-20 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA20-BR010-750-CI2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
367 | Tauhara B Steamfield | Separation Plant Steam System | 20CP023 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 15 | +/- 1% | TH00S020NAA20CP023 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-20 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA20-BR010-750-CI2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
368 | Tauhara B Steamfield | Separation Plant Steam System | 20CP031 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - | FALSE | FALSE | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 13 | +/- 1% | TH00S020NAA20CP031 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-20 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA20-BR010-750-CI2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.25 | 6.5 | 9.75 | 13 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
369 | Tauhara B Steamfield | Separation Plant Steam System | 20CP032 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - | FALSE | FALSE | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 13 | +/- 1% | TH00S020NAA20CP032 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-20 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA20-BR010-750-CI2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.25 | 6.5 | 9.75 | 13 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
370 | Tauhara B Steamfield | Separation Plant Steam System | 20CP033 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - | FALSE | FALSE | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 13 | +/- 1% | TH00S020NAA20CP033 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-20 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA20-BR010-750-CI2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.25 | 6.5 | 9.75 | 13 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
371 | Tauhara B Steamfield | Separation Plant Steam System | 31CF010 | - | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0 | - | FALSE | FALSE | 162 | 0 to 216 | Separation Plant - Flow | -edit- | 0 to 216 | +/- 1% | TH00S020NAA31CF010 | CCI-DAT-1478 | PO# 4500191995 | PRO-PID-22 | rev: 5.6 instment type: Flow Transmitter (Vortex) make: InnovaMass Vendor: Custom Controls drwg: MEC-DET-1045 line # S020NAA31-BR010-1300-CL2 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 54 | 108 | 162 | 216 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
372 | Tauhara B Steamfield | Separation Plant Steam System | 31CL410 | - | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020NAA31CL410 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-22 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type LP10 line # S020NAA31-BR410-1050-CL2 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 250 | 500 | 750 | 1000 | 0 | 0 | 250 | 500 | 750 | 1000 | [9 empty] | FALSE
373 | Tauhara B Steamfield | Separation Plant Steam System | 31CL450 | - | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020NAA31CL450 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-23 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type LP10 line # S020NAA31-BR450-1050-CL2 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 250 | 500 | 750 | 1000 | 0 | 0 | 250 | 500 | 750 | 1000 | [9 empty] | FALSE
374 | Tauhara B Steamfield | Separation Plant Steam System | 31CL460 | - | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020NAA31CL460 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-23 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type LP10 line # S020NAA31-BR460-1050-CL2 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 250 | 500 | 750 | 1000 | 0 | 0 | 250 | 500 | 750 | 1000 | [9 empty] | FALSE
375 | Tauhara B Steamfield | Separation Plant Steam System | 31CP021 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA31CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA31-BR010-1050-CL2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
376 | Tauhara B Steamfield | Separation Plant Steam System | 31CP022 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA31CP022 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA31-BR010-1050-CL2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
377 | Tauhara B Steamfield | Separation Plant Steam System | 31CP023 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA31CP023 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA31-BR010-1050-CL2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
378 | Tauhara B Steamfield | Separation Plant Steam System | 31CP031 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA31CP031 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA31-BR010-1050-CL2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
379 | Tauhara B Steamfield | Separation Plant Steam System | 31CP032 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA31CP032 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA31-BR010-1050-CL2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
380 | Tauhara B Steamfield | Separation Plant Steam System | 31CP033 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA31CP033 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA31-BR010-1050-CL2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
381 | Tauhara B Steamfield | Separation Plant Steam System | 32CF010 | - | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0 | - | FALSE | FALSE | 162 | 0 to 216 | Separation Plant - Flow | -edit- | 0 to 216 | +/- 1% | TH00S020NAA32CF010 | CCI-DAT-1478 | PO# 4500191995 | PRO-PID-24 | rev: 5.6 instment type: Flow Transmitter (Vortex) make: InnovaMass Vendor: Custom Controls drwg: MEC-DET-1045 line # S020NAA32-BR010-1300-CL2 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 54 | 108 | 162 | 216 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
382 | Tauhara B Steamfield | Separation Plant Steam System | 32CL410 | - | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020NAA32CL410 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-24 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type LP10 line # S020NAA32-BR410-1050-CL2 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 250 | 500 | 750 | 1000 | 0 | 0 | 250 | 500 | 750 | 1000 | [9 empty] | FALSE
383 | Tauhara B Steamfield | Separation Plant Steam System | 32CL450 | - | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020NAA32CL450 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-25 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type LP10 line # S020NAA32-BR450-1050-CL2 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 250 | 500 | 750 | 1000 | 0 | 0 | 250 | 500 | 750 | 1000 | [9 empty] | FALSE
384 | Tauhara B Steamfield | Separation Plant Steam System | 32CL460 | - | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - | FALSE | FALSE |  | - | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020NAA32CL460 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-25 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type LP10 line # S020NAA32-BR460-1050-CL2 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 250 | 500 | 750 | 1000 | 0 | 0 | 250 | 500 | 750 | 1000 | [9 empty] | FALSE
385 | Tauhara B Steamfield | Separation Plant Steam System | 32CP021 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA32CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA32-BR010-1050-CL2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
386 | Tauhara B Steamfield | Separation Plant Steam System | 32CP022 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA32CP022 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA32-BR010-1050-CL2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
387 | Tauhara B Steamfield | Separation Plant Steam System | 32CP023 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA32CP023 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA32-BR010-1050-CL2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
388 | Tauhara B Steamfield | Separation Plant Steam System | 32CP031 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA32CP031 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA32-BR010-1050-CL2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
389 | Tauhara B Steamfield | Separation Plant Steam System | 32CP032 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA32CP032 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA32-BR010-1050-CL2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
390 | Tauhara B Steamfield | Separation Plant Steam System | 32CP033 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA32CP033 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NAA32-BR010-1050-CL2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
391 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL011 | - | Rosemount 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA10CL011 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-12 | rev: 3.2 instment type: Level Transmitter (GW Radar) make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1052 line # S020NDA10-BR311-80-CH4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
392 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL012 | - | Rosemount 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA10CL012 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-12 | rev: 3.2 instment type: Level Transmitter (GW Radar) make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1052 line # S020NDA10-BR312-80-CH4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
393 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL013 | - | Rosemount 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA10CL013 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-12 | rev: 3.2 instment type: Level Transmitter (GW Radar) make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1052 line # S020NDA10-BR313-80-CH4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
394 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL014 | - | Rosemount 3051S2CD3A2B12A1BM5Q4Q8Q15 | - | FALSE | FALSE | - | 0 to 5690 | Separation Plant - Level | -edit- | 0 to 5690 | +/- 1% | TH00S020NDA10CL014 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-12 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 MEC-SCN-3036 line # S020NDA10-BR313-80-CH4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1422.5 | 2845 | 4267.5 | 5690 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
395 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL021 | - | Rosemount 3051S2CD2A2B12A1BM5Q4Q8Q15 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA10CL021 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-12 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1050 line # S020NDA10-BR333-80-CH4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
396 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL022 | - | Rosemount 3051S2CD2A2B12A1BM5Q4Q8Q15 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA10CL022 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-12 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1050 line # S020NDA10-BR332-80-CH4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
397 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL023 | - | Rosemount 3051S2CD2A2B12A1BM5Q4Q8Q15 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA10CL023 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-12 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1050 line # S020NDA10-BR331-80-CH4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
398 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL031 | - | Bliss Anand R/88/M/S/2/1/B/N/N/X/PN/S/2560MM | - | FALSE | FALSE | 1676 | - | Separation Plant - Level | -edit- | 335 to 3018 | +/- 1% | TH00S020NDA10CL031 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-12 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: CCI-DET-2705 NDA-MEC-DET-1050 line # S020NDA10-BR331-80-CH4 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 670 | 1340 | 2010 | 2680 | 0 | 0 | 670 | 1340 | 2010 | 2680 | [9 empty] | FALSE
399 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NDA10-BR013-1050-CH2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
400 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 217.9 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-11 | rev: 4.8 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020NDA10-BR011-750-CH2 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
401 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CT020 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 217.9 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NDA10CT020 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-11 | rev: 4.8 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020NDA10-BR012-800-CH2 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
402 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 217.9 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NDA10CT030 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-11 | rev: 4.8 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020NDA10-BR013-1050-CH2 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
403 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 2530 | 0 to 3222 | Separation Plant - Flow | -edit- | 0 to 3222 | +/- 1% | TH00S020NDA20CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-12 | rev: 6.3 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # S020NDA20-BR010-900-CH4 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 805.5 | 1611 | 2416.5 | 3222 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
404 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CF020 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 2916 | 0 to 3222 | Separation Plant - Flow | -edit- | 0 to 3222 | +/- 1% | TH00S020NDA20CF020 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-12 | rev: 6.3 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # S020NDA20-BR010-900-CH4 | tph | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 805.5 | 1611 | 2416.5 | 3222 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
405 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL011 | - | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA20CL011 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-13 | rev: 3.2 instment type: Level Transmitter (GW Radar) make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1055 line # S020NDA20-BR311-80-CI4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
406 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL012 | - | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA20CL012 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-13 | rev: 3.2 instment type: Level Transmitter (GW Radar) make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1055 line # S020NDA20-BR312-80-CI4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
407 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL013 | - | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA20CL013 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-13 | rev: 3.2 instment type: Level Transmitter (GW Radar) make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1055 line # S020NDA20-BR313-80-CI4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
408 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL014 | - | Rosemount 3051S2CD3A2B12A1BM5Q4Q8Q15 | - | FALSE | FALSE | - | 0 to 5440 | Separation Plant - Level | -edit- | 0 to 5440 | +/- 1% | TH00S020NDA20CL014 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-13 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 MEC-SCN-3038 line # S020NDA20-BR313-80-CI4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1360 | 2720 | 4080 | 5440 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
409 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL021 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA20CL021 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-13 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1053 line # S020NDA20-BR333-80-CI4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
410 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL022 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA20CL022 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-13 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1053 line # S020NDA20-BR332-80-CI4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
411 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL023 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA20CL023 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-13 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1053 line # S020NDA20-BR331-80-CI4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
412 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL031 | - | Bliss Anand R/88/M/S/2/1/B/N/N/X/PN/S/2560MM | - | FALSE | FALSE | 1676 | - | Separation Plant - Level | -edit- | 335 to 3018 | +/- 1% | TH00S020NDA20CL031 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-13 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: CCI-DET-2705 NDA-MEC-DET-1053 line # S020NDA20-BR331-80-CI4 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 670 | 1340 | 2010 | 2680 | 0 | 0 | 670 | 1340 | 2010 | 2680 | [9 empty] | FALSE
413 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 15 | +/- 1% | TH00S020NDA20CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-13 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NDA20-BR021-750-CI1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
414 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CR001 | - | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - | FALSE | FALSE | * | TBC | Separation Plant - Corrosometer | -edit- | TBC | +/- 1% | TH00S020NDA20CR001 | COSASCO Model 3500/3500HT ER-420 | PO# 4500189863 | PRO-PID-12 | rev: 5.6 instment type: Corrosometer make: Cosasco Vendor: Cosasco drwg: TBC line # S020NDA20-BR010-900-CH4 | mm/Time Unit | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
415 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CR002 | - | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - | FALSE | FALSE | * | TBC | Separation Plant - Corrosometer | -edit- | TBC | +/- 1% | TH00S020NDA20CR002 | COSASCO Model 3500/3500HT ER-420 | PO# 4500189863 | PRO-PID-12 | rev: 5.6 instment type: Corrosometer make: Cosasco Vendor: Cosasco drwg: TBC line # S020NDA20-BR010-900-CH4 | mm/Time Unit | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
416 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CR003 | - | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - | FALSE | FALSE | * | TBC | Separation Plant - Corrosometer | -edit- | TBC | +/- 1% | TH00S020NDA20CR003 | COSASCO Model 3500/3500HT ER-420 | PO# 4500189863 | PRO-PID-12 | rev: 5.6 instment type: Corrosometer make: Cosasco Vendor: Cosasco drwg: TBC line # S020NDA20-BR010-900-CH4 | mm/Time Unit | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
417 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CR004 | - | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - | FALSE | FALSE | * | TBC | Separation Plant - Corrosometer | -edit- | TBC | +/- 1% | TH00S020NDA30CR004 | COSASCO Model 3500/3500HT ER-420 | PO# 4500189863 | PRO-PID-13 | rev: 6.5 instment type: Corrosometer make: Cosasco Vendor: Cosasco drwg: 1" NPT line # S020NDA30-BR010-900-CL4 | mm/Time Unit | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
418 | Tauhara B Steamfield | Separation Plant Production Piping System | 21CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 450 | 0 to 495 | Separation Plant - Flow | -edit- | 0 to 495 | +/- 1% | TH00S020NDA21CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-30 | rev: 5.6 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # S020NDA21-BR021-80-CH4 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 123.75 | 247.5 | 371.25 | 495 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 15 | L/min |  |  | FALSE
419 | Tauhara B Steamfield | Separation Plant Production Piping System | 21CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 25 | +/- 1% | TH00S020NDA21CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-30 | rev: 5.6 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NDA21-BR011-100-CH4 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
420 | Tauhara B Steamfield | Separation Plant Production Piping System | 21CP011 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 18.8 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 25 | +/- 1% | TH00S020NDA21CP011 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-30 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2701 line # S020NDA21-BR021-80-CH4 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
421 | Tauhara B Steamfield | Separation Plant Production Piping System | 21CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 202 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NDA21CT010 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-30 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020NDA21-BR011-100-CH4 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 200 | [5 empty] | FALSE
422 | Tauhara B Steamfield | Separation Plant Production Piping System | 22CF020 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | FALSE | FALSE | 450 | 0 to 495 | Separation Plant - Flow | -edit- | 0 to 495 | +/- 1% | TH00S020NDA22CF020 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-30 | rev: 5.6 instment type: Flow Transmitter (Orifice Flow) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 line # S020NDA22-BR022-80-CH4 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 123.75 | 247.5 | 371.25 | 495 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 15 | L/min |  |  | FALSE
423 | Tauhara B Steamfield | Separation Plant Production Piping System | 22CP020 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 25 | +/- 1% | TH00S020NDA22CP020 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-30 | rev: 5.6 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NDA22-BR012-100-CH4 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
424 | Tauhara B Steamfield | Separation Plant Production Piping System | 22CP021 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 18.8 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 25 | +/- 1% | TH00S020NDA22CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-30 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2701 line # S020NDA22-BR022-80-CH4 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
425 | Tauhara B Steamfield | Separation Plant Production Piping System | 22CT020 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 202 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NDA22CT020 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-30 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020NDA22-BR012-100-CH4 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 200 | [5 empty] | FALSE
426 | Tauhara B Steamfield | Separation Plant Production Piping System | 23CF011 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - | FALSE | FALSE | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | Refer to Specification | +/- 1% | TH00S020NDA23CF011 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-101 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDA23-BR602-15-S10 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8 |  | 2 |  |  |  | FALSE
427 | Tauhara B Steamfield | Separation Plant Production Piping System | 23CP511 | - | Rosemount 3051CD3A02A1BS5M4Q4Q8T1Q15 | - | FALSE | FALSE | 0.23 | 0 to 20 | Separation Plant - Pressure | -edit- | 0 to 20 | +/- 1% | TH00S020NDA23CP511 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-101 | rev: 5.6 instment type: Pressure Differential Transmitter make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDA23-BR602-15-S10 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 5 | 10 | 15 | 20 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 2 | [5 empty] | FALSE
428 | Tauhara B Steamfield | Separation Plant Production Piping System | 23CP512 | - | Wika 72039878+14503369+0731277 | - | FALSE | FALSE | 8 | 0 to 25 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020NDA23CP512 | QCM-PRO-SPC-0109 | PO# 4500198881 | PRO-PID-101 | rev: 7.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: Vendor Designed line # S020NDA23-BR602-15-S10 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | FALSE
429 | Tauhara B Steamfield | Separation Plant Production Piping System | 23CQ010 | - | E+H CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 | - | FALSE | FALSE | 5 | 0 to 14 | Separation Plant - Analyser | -edit- | 3.5 to 8.5 | +/- 1% | TH00S020NDA23CQ010 | QCM-PRO-SPC-0109 | PO# 4500191501 | PRO-PID-101 | rev: instment type: Analyser Transmitter (pH) make: E+H Vendor: EMC drwg: Vendor Designed line # S020NDA23-BR602-15-S10 | pH | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 3.5 | 4.75 | 6 | 7.25 | 8.5 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 5.5 |  | 4.5 |  |  |  | FALSE
430 | Tauhara B Steamfield | Separation Plant Production Piping System | 23CT011 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 60 | 0 to 215 | Separation Plant - Temperature | -edit- | 0 to 100 | +/- 1% | TH00S020NDA23CT011 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-101 | rev: 4.6 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDA23-BR602-15-S10 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | 50 |  |  |  |  | FALSE
431 | Tauhara B Steamfield | Separation Plant Production Piping System | 24CF020 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - | FALSE | FALSE | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | Refer to Specification | +/- 1% | TH00S020NDA24CF020 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-101 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDA24-BR603-15-S10 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8 |  | 2 |  |  |  | FALSE
432 | Tauhara B Steamfield | Separation Plant Production Piping System | 24CP521 | - | Rosemount 3051CD3A02A1BS5M4Q4Q8T1Q15 | - | FALSE | FALSE | 0.23 | 0 to 20 | Separation Plant - Pressure | -edit- | 0 to 20 | +/- 1% | TH00S020NDA24CP521 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-101 | rev: 5.6 instment type: Pressure Differential Transmitter make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDA24-BR603-15-S10 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 5 | 10 | 15 | 20 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 2 | [5 empty] | FALSE
433 | Tauhara B Steamfield | Separation Plant Production Piping System | 24CP522 | - | Wika 72039878+14503369+0731277 | - | FALSE | FALSE | 8 | 0 to 25 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020NDA24CP522 | QCM-PRO-SPC-0109 | PO# 4500198881 | PRO-PID-101 | rev: 7.5 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: Vendor Designed line # S020NDA24-BR603-15-S10 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | FALSE
434 | Tauhara B Steamfield | Separation Plant Production Piping System | 24CQ020 | - | E+H CM442-EL64/0 + CPS47E-10C2/0 | - | FALSE | FALSE | 5 | 0 to 14 | Separation Plant - Analyser | -edit- | 3.5 to 8.5 | +/- 1% | TH00S020NDA24CQ020 | QCM-PRO-SPC-0109 | PO# 4500191501 | PRO-PID-101 | rev: instment type: Analyser Transmitter (pH) make: E+H Vendor: EMC drwg: Vendor Designed line # S020NDA24-BR603-15-S10 | pH | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 3.5 | 4.75 | 6 | 7.25 | 8.5 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 5.5 |  | 4.5 |  |  |  | FALSE
435 | Tauhara B Steamfield | Separation Plant Production Piping System | 24CT021 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 60 | 0 to 215 | Separation Plant - Temperature | -edit- | 0 to 100 | +/- 1% | TH00S020NDA24CT021 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-101 | rev: 4.6 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDA24-BR603-15-S10 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | 50 |  |  |  |  | FALSE
436 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL011 | - | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA30CL011 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-14 | rev: 3.2 instment type: Level Transmitter (GW Radar) make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1055 line # S020NDA30-BR311-80-CL4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
437 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL012 | - | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA30CL012 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-14 | rev: 3.2 instment type: Level Transmitter (GW Radar) make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1055 line # S020NDA30-BR312-80-CL4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
438 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL013 | - | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA30CL013 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-14 | rev: 3.2 instment type: Level Transmitter (GW Radar) make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1055 line # S020NDA30-BR313-80-CL4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
439 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL014 | - | Rosemount 3051S2CD3A2B12A1BM5Q4Q8Q15 | - | FALSE | FALSE | - | 0 to 5640 | Separation Plant - Level | -edit- | 0 to 5640 | +/- 1% | TH00S020NDA30CL014 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-14 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 MEC-SCN-3039 line # S020NDA30-BR313-80-CL4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1410 | 2820 | 4230 | 5640 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
440 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL015 | - | Rosemount 3051S2CD3A2B12A1BM5Q4Q8Q15 | - | FALSE | FALSE | - | 0 to 5640 | Separation Plant - Level | -edit- | 0 to 5640 | +/- 1% | TH00S020NDA30CL015 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-14 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 line # S020NDA30-BR313-80-CL4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1410 | 2820 | 4230 | 5640 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
441 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL021 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA30CL021 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-14 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1053 line # S020NDA30-BR333-80-CL4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
442 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL022 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA30CL022 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-14 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1053 line # S020NDA30-BR332-80-CL4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
443 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL023 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | FALSE | FALSE | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA30CL023 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-14 | rev: 7.0 instment type: Level Transmitter (DP) make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1053 line # S020NDA30-BR331-80-CL4 | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
444 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL031 | - | Bliss Anand R/88/M/S/2/1/B/N/N/X/PN/S/2560MM | - | FALSE | FALSE | 1676 | - | Separation Plant - Level | -edit- | 335 to 3018 | +/- 1% | TH00S020NDA30CL031 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-14 | rev: 6.0 instment type: Level Gauge make: Bliss Anand Vendor: Powerflo Solutions drwg: CCI-DET-2705 NDA-MEC-DET-1053 line # S020NDA30-BR331-80-CL4 | mm | mm | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 670 | 1340 | 2010 | 2680 | 0 | 0 | 670 | 1340 | 2010 | 2680 | [9 empty] | FALSE
445 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CP011 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NDA30CP011 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 6.2 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NDA30-BR021-1050-CL1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
446 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CP012 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NDA30CP012 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NDA30-BR023-1050-CL1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
447 | Tauhara B Steamfield | Separation Plant Separated Water System | 10CP010 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 2.6 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 10 | +/- 1% | TH00S020NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020NDB10-BR010-900-CL4 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
448 | Tauhara B Steamfield | Separation Plant Separated Water System | 11CF011 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - | FALSE | FALSE | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | 0 to 10 | +/- 1% | TH00S020NDB11CF011 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDB11-BR601-15-S10 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8 |  | 2 |  |  |  | FALSE
449 | Tauhara B Steamfield | Separation Plant Separated Water System | 11CQ010 | - | E+H CM442-EL64/0 + CPS47E-10C2/0 | - | FALSE | FALSE | 5 | 0 to 14 | Separation Plant - Analyser | -edit- | 3.5 to 8.5 | +/- 1% | TH00S020NDB11CQ010 | QCM-PRO-DAT-0108 | PO# 4500191501 | PRO-PID-100 | rev: instment type: Analyser Transmitter (pH) make: E+H Vendor: EMC drwg: Vendor Designed line # S020NDB11-BR601-15-S10 | pH | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 3.5 | 4.75 | 6 | 7.25 | 8.5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
450 | Tauhara B Steamfield | Separation Plant Separated Water System | 11CT011 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 60 | 0 to 75 | Separation Plant - Temperature | -edit- | 0 to 100 | +/- 1% | TH00S020NDB11CT011 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 4.6 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDB11-BR601-15-S10 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | 50 |  |  |  |  | FALSE
451 | Tauhara B Steamfield | Separation Plant Separated Water System | 12CF021 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - | FALSE | FALSE | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | Refer to Specification | +/- 1% | TH00S020NDB12CF021 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDB12-BR602-15-S10 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8 |  | 2 |  |  |  | FALSE
452 | Tauhara B Steamfield | Separation Plant Separated Water System | 12CQ020 | - | E+H CM442-EL64/0 + CPS47E-10C2/0 | - | FALSE | FALSE | 5 | 0 to 14 | Separation Plant - Analyser | -edit- | 3.5 to 8.5 | +/- 1% | TH00S020NDB12CQ020 | QCM-PRO-SPC-0109 | PO# 4500191501 | PRO-PID-100 | rev: instment type: Analyser Transmitter (pH) make: E+H Vendor: EMC drwg: Vendor Designed line # S020NDB12-BR602-15-S10 | pH | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 3.5 | 4.75 | 6 | 7.25 | 8.5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
453 | Tauhara B Steamfield | Separation Plant Separated Water System | 12CT021 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 60 | 0 to 75 | Separation Plant - Temperature | -edit- | 0 to 100 | +/- 1% | TH00S020NDB12CT021 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 4.6 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDB12-BR602-15-S10 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | 50 |  |  |  |  | FALSE
454 | Tauhara B Steamfield | Separation Plant Separated Water System | 13CF031 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - | FALSE | FALSE | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | Refer to Specification | +/- 1% | TH00S020NDB13CF031 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDB13-BR603-15-S10 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8 |  | 2 |  |  |  | FALSE
455 | Tauhara B Steamfield | Separation Plant Separated Water System | 13CQ030 | - | E+H CM442-EL64/0 | - | FALSE | FALSE | 5 | 0 to 14 | Separation Plant - Analyser | -edit- | 3.5 to 8.5 | +/- 1% | TH00S020NDB13CQ030 | QCM-PRO-SPC-0109 | PO# 4500191501 | PRO-PID-100 | rev: instment type: Analyser Transmitter (pH) make: E+H Vendor: EMC drwg: Vendor Designed line # S020NDB13-BR603-15-S10 | pH | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 3.5 | 4.75 | 6 | 7.25 | 8.5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
456 | Tauhara B Steamfield | Separation Plant Separated Water System | 13CT031 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 60 | 0 to 75 | Separation Plant - Temperature | -edit- | 0 to 100 | +/- 1% | TH00S020NDB13CT031 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 4.6 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDB13-BR603-15-S10 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | 50 |  |  |  |  | FALSE
457 | Tauhara B Steamfield | Separation Plant Separated Water System | 14CF041 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - | FALSE | FALSE | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | Refer to Specification | +/- 1% | TH00S020NDB14CF041 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 5.6 instment type: Flow Transmitter (Magnetic) make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDB14-BR604-15-S10 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8 |  | 2 |  |  |  | FALSE
458 | Tauhara B Steamfield | Separation Plant Separated Water System | 14CQ040 | - | E+H CM442-EL64/0 | - | FALSE | FALSE | 5 | 0 to 14 | Separation Plant - Analyser | -edit- | 3.5 to 8.5 | +/- 1% | TH00S020NDB14CQ040 | QCM-PRO-SPC-0109 | PO# 4500191501 | PRO-PID-100 | rev: instment type: Analyser Transmitter (pH) make: E+H Vendor: EMC drwg: Vendor Designed line # S020NDB14-BR604-15-S10 | pH | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 3.5 | 4.75 | 6 | 7.25 | 8.5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
459 | Tauhara B Steamfield | Separation Plant Separated Water System | 14CT041 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 60 | 0 to 75 | Separation Plant - Temperature | -edit- | 0 to 100 | +/- 1% | TH00S020NDB14CT041 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 4.6 instment type: Temperature Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: Vendor Designed line # S020NDB14-BR604-15-S10 | °C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | 50 |  |  |  |  | FALSE
460 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CL010 | - | Vega PS31.XXXXXGMHB +GFLK.ADGX | - | FALSE | FALSE |  | 0 to 4500 | Separation Plant - Level | -edit- | TBC | +/- 1% | TH00S020QCM10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-29 | rev: 6.5 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: Nozzle mount QCM-PRO-DAT-0071 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1125 | 2250 | 3375 | 4500 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 95 | 95 | 10 |  |  |  | FALSE
461 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CL020 | - | Vega PS31.XXXXXGMHB +GFLK.ADGX | - | FALSE | FALSE |  | 0 to 4500 | Separation Plant - Level | -edit- | TBC | +/- 1% | TH00S020QCM10CL020 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-29 | rev: 6.5 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: Nozzle mount QCM-PRO-DAT-0071 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1125 | 2250 | 3375 | 4500 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 95 | 95 | 10 |  |  |  | FALSE
462 | Tauhara B Steamfield | !@! Separation Plant Acid Dosing System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 20 | -5 to 50 | Separation Plant - Temperature | -edit- | -5 to 50 | +/- 1% | TH00S020QCM10CT010 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-29 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 QCM-PRO-DAT-0071 line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -5 | 8.75 | 22.5 | 36.25 | 50 | 0 | -5 | 8.75 | 22.5 | 36.25 | 50 | [9 empty] | FALSE
463 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10DL0020 | - | Vega TKALM3-HMI-DB | - | FALSE | FALSE |  | See notes | Separation Plant - Level | -edit- | 0-100% | +/- 1% | TH00S020QCM10DL0020 | CCI-DAT-1470 | PO# 4500189544 | PRO-PID-29 | rev: 3.2 instment type: Level Indicator (Remote) make: Vega Vendor: Instrumatics drwg: CCI-DET-2720 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
464 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10EH011 | - | Vega See S020QCM10DL0020 | - | FALSE | FALSE |  |  | Separation Plant - Level | -edit- |  | +/- 1% | TH00S020QCM10EH011 |  | PO# 4500189544 | PRO-PID-29 | rev: 3.2 instment type: Level Sounder Beacon (Remote) make: Vega Vendor: Instrumatics drwg: CCI-DET-2720 line # | mm | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | FALSE
465 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CF010 | - | Yokogawa AX005-GA000BA2AT224B-2JA11/GRT | - | FALSE | FALSE | 2.2 | 0-3 | Separation Plant - Flow | -edit- | 0 to 2.5 | +/- 1% | TH00S020QCM20CF010 | CCI-DAT-1474 | PO# 4500201023 | PRO-PID-30 | rev: 7.1 instment type: Flow Transmitter (Magnetic) make: Yokogawa Vendor: Yokogawa drwg: CCI-DET-2707 line # S020QCM20-BR011-15-S2 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0.625 | 1.25 | 1.875 | 2.5 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 2 |  | 0.5 |  |  |  | FALSE
466 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CP011 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 18.4 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 30 | +/- 1% | TH00S020QCM20CP011 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-30 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020QCM20-BR011-25-S2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 7.5 | 15 | 22.5 | 30 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 27 | [5 empty] | FALSE
467 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CP501 | - | Wika 72039899+14503369+ | - | FALSE | FALSE | 0.3 | 0 to 5 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020QCM20CP501 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-30 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020QCM20-BR010-50-S2 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | [9 empty] | FALSE
468 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CP510 | - | Wika 72039915 (Model 433.56.100)+14503369 (Model IV10)+ | - | FALSE | FALSE | 18.4 | 0 to 40 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020QCM20CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-30 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020QCM20-BR011-25-S2 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 10 | 20 | 30 | 40 | 0 | 0 | 10 | 20 | 30 | 40 | [9 empty] | FALSE
469 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 20 | -5 to 50 | Separation Plant - Temperature | -edit- | -5 to 50 | +/- 1% | TH00S020QCM20CT010 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-30 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020QCM20-BR011-25-S2 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -5 | 8.75 | 22.5 | 36.25 | 50 | 0 | -5 | 8.75 | 22.5 | 36.25 | 50 | [9 empty] | FALSE
470 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CF020 | - | Yokogawa AX005-GA000BA2AT224B-2JA11/GRT | - | FALSE | FALSE | 2.2 | 0-3 | Separation Plant - Flow | -edit- | 0 to 2.5 | +/- 1% | TH00S020QCM21CF020 | CCI-DAT-1474 | PO# 4500201023 | PRO-PID-30 | rev: 7.1 instment type: Flow Transmitter (Magnetic) make: Yokogawa Vendor: Yokogawa drwg: CCI-DET-2707 line # S020QCM21-BR021-15-S2 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0.625 | 1.25 | 1.875 | 2.5 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 2 |  | 0.5 |  |  |  | FALSE
471 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CF010Temp | - | IFM SI5004+E40107 | - | FALSE | FALSE | 2.2 | 0-3 | Separation Plant - Flow | -edit- | 0 to 2.5 | +/- 1% | TH00S020QCM21CF010Temp | CCI-DAT-1474 | PO# 4500200797 | PRO-PID-30 | rev: 7.0 instment type: Flow Transmitter (Magnetic) make: IFM Vendor: IFM drwg: CCI-DET-2707 line # S020QCM21-BR021-15-S2 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0.625 | 1.25 | 1.875 | 2.5 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
472 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CF020Temp | - | IFM SI5004+E40107 | - | FALSE | FALSE | 2.2 | 0-3 | Separation Plant - Flow | -edit- | 0 to 2.5 | +/- 1% | TH00S020QCM21CF020Temp | CCI-DAT-1474 | PO# 4500200797 | PRO-PID-30 | rev: 7.0 instment type: Flow Transmitter (Magnetic) make: IFM Vendor: IFM drwg: CCI-DET-2707 line # S020QCM21-BR021-15-S2 | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0.625 | 1.25 | 1.875 | 2.5 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
473 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CP021 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 18.4 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 30 | +/- 1% | TH00S020QCM21CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-30 | rev: 3.8 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # S020QCM21-BR021-25-S2 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 7.5 | 15 | 22.5 | 30 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 27 | [5 empty] | FALSE
474 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CP502 | - | Wika 72039899+14503369+ | - | FALSE | FALSE | 0.3 | 0 to 5 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020QCM21CP502 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-30 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020QCM21-BR020-50-S2 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | [9 empty] | FALSE
475 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CP520 | - | Wika 72039915 (Model 433.56.100)+14503369 (Model IV10)+ | - | FALSE | FALSE | 18.4 | 0 to 40 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020QCM21CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-30 | rev: 3.2 instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # S020QCM21-BR021-25-S2 | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 10 | 20 | 30 | 40 | 0 | 0 | 10 | 20 | 30 | 40 | [9 empty] | FALSE
476 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CT020 | - | Rosemount 644HANAJ1M4Q4T1 | - | FALSE | FALSE | 20 | -5 to 50 | Separation Plant - Temperature | -edit- | -5 to 50 | +/- 1% | TH00S020QCM21CT020 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-30 | rev: 6.6 instment type: Temperature Element make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 line # S020QCM21-BR021-25-S2 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -5 | 8.75 | 22.5 | 36.25 | 50 | 0 | -5 | 8.75 | 22.5 | 36.25 | 50 | [9 empty] | FALSE
477 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 30CL031 | - | Vega PS21.XXXXXGMHB+MBA.BB | - | FALSE | FALSE |  | 0 to 1500 | Separation Plant - Level | -edit- | 0 to 1500 | +/- 1% | TH00S020QCM30CL031 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-29 | rev: 3.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 375 | 750 | 1125 | 1500 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
478 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 30CL032 | - | Vega PS21.XXXXXGMHB+MBA.BB | - | FALSE | FALSE |  | 0 to 1500 | Separation Plant - Level | -edit- | 0 to 1500 | +/- 1% | TH00S020QCM30CL032 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-29 | rev: 3.2 instment type: Level Transmitter (Radar) make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 line # | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 375 | 750 | 1125 | 1500 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
479 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 30CQ010 | - | E+H CLS50D-1009/0 + CYA112-1V02/0 | - | FALSE | FALSE | TBC | TBC | Separation Plant - Analyser | -edit- | TBC | +/- 1% | TH00S020QCM30CQ010 | See notes | PO# 4500191348 | PRO-PID-29 | rev: 5.6 instment type: Analyser Transmitter (Conductivity) make: E+H Vendor: EMC drwg: See notes line # | uS/cm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
480 | Tauhara B Steamfield | Pump Station Fire Water | 10CP401 | - | Wika 72039878+14503369 | - | FALSE | FALSE | - | 0 to 16 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00S020SGA10CP401 | CCI-DAT-1460 | PO# 4500193000 | PRO-PID-50 | rev: instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4 | 8 | 12 | 16 | 0 | 0 | 4 | 8 | 12 | 16 | [9 empty] | FALSE
481 | Tauhara B Steamfield | Pump Station Fire Water | 10CP402 | - | Wika 72039878+14503369 | - | FALSE | FALSE | - | 0 to 16 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00S020SGA10CP402 | CCI-DAT-1460 | PO# 4500193000 | PRO-PID-50 | rev: instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4 | 8 | 12 | 16 | 0 | 0 | 4 | 8 | 12 | 16 | [9 empty] | FALSE
482 | Tauhara B Steamfield | Pump Station Fire Water | 10CP405 | - | Wika 72039878+14503369 | - | FALSE | FALSE | - | 0 to 16 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00S020SGA10CP405 | CCI-DAT-1460 | PO# 4500193000 | PRO-PID-50 | rev: instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4 | 8 | 12 | 16 | 0 | 0 | 4 | 8 | 12 | 16 | [9 empty] | FALSE
483 | Tauhara B Steamfield | Pump Station Fire Water | 10CP406 | - | Wika 72039878+14503369 | - | FALSE | FALSE | - | 0 to 16 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00S020SGA10CP406 | CCI-DAT-1460 | PO# 4500193000 | PRO-PID-50 | rev: instment type: Pressure Gauge make: Wika Vendor: Wika drwg: CCI-DET-2701 line # | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 4 | 8 | 12 | 16 | 0 | 0 | 4 | 8 | 12 | 16 | [9 empty] | FALSE
484 | Tauhara B Steamfield | Separation Plant Room Temperature | 10CT001 | - | E+H TST434-J1A3B0 | - | FALSE | FALSE | - | TBC | Separation Plant - Temperature | -edit- | TBC | +/- 1% | TH00S020SAA10CT001 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 instment type: Temperature Element make: E+H Vendor: EMC drwg: line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | FALSE
485 | Tauhara B Steamfield | Separation Plant Room Temperature | 10CT002 | - | E+H TST434-J1A3B0 | - | FALSE | FALSE | - | TBC | Separation Plant - Temperature | -edit- | TBC | +/- 1% | TH00S020SAA10CT002 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 instment type: Temperature Element make: E+H Vendor: EMC drwg: line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | FALSE
486 | Tauhara B Steamfield | Separation Plant Room Temperature | 10CT003 | - | E+H TST434-J1A3B0 | - | FALSE | FALSE | - | TBC | Separation Plant - Temperature | -edit- | TBC | +/- 1% | TH00S020SAA10CT003 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 instment type: Temperature Element make: E+H Vendor: EMC drwg: line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | FALSE
487 | Tauhara B Steamfield | Pump Station Room Temperature | 10CT001 | - | E+H TST434-J1A3B0 | - | FALSE | FALSE | - | TBC | Pump Station - Temperature | -edit- | TBC | +/- 1% | TH00P020SAA10CT001 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 instment type: Temperature Element make: E+H Vendor: EMC drwg: line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | FALSE
488 | Tauhara B Steamfield | Pump Station Room Temperature | 10CT002 | - | E+H TST434-J1A3B0 | - | FALSE | FALSE | - | TBC | Pump Station - Temperature | -edit- | TBC | +/- 1% | TH00P020SAA10CT002 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 instment type: Temperature Element make: E+H Vendor: EMC drwg: line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | FALSE
489 | Tauhara B Steamfield | Pump Station Room Temperature | 10CT003 | - | E+H TST434-J1A3B0 | - | FALSE | FALSE | - | TBC | Pump Station - Temperature | -edit- | TBC | +/- 1% | TH00P020SAA10CT003 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 instment type: Temperature Element make: E+H Vendor: EMC drwg: line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | FALSE
490 | Tauhara B Steamfield | Pump Station Room Temperature | 10CT004 | - | E+H TST434-J1A3B0 | - | FALSE | FALSE | - | TBC | Pump Station - Temperature | -edit- | TBC | +/- 1% | TH00P020SAA10CT004 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 instment type: Temperature Element make: E+H Vendor: EMC drwg: line # | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | FALSE
491 | Tauhara B Steamfield | TH11 110VDC System - Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 150 V | TH11 110VDC System - Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH000110BTL10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | FALSE
492 | Tauhara B Steamfield | TH11 110VDC System - Current Battery Systems | 10CE201 | Indication | ? | C | FALSE | FALSE | - | 0 to 150 A | TH11 110VDC System - Current - - | -edit- | 0 to 150 A | +/- 1% | TH000110BTL10CE201 | - |  | - |  | Amps | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
493 | Tauhara B Steamfield | TH12 110VDC System - Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 150 V | TH12 110VDC System - Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH000120BTL10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | FALSE
494 | Tauhara B Steamfield | TH12 110VDC System - Current Battery Systems | 10CE201 | Indication | ? | C | FALSE | FALSE | - | 0 to 150 A | TH12 110VDC System - Current - - | -edit- | 0 to 150 A | +/- 1% | TH000120BTL10CE201 | - |  | - |  | Amps | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
495 | Tauhara B Steamfield | TH26 110VDC System - Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 150 V | TH26 110VDC System - Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH000260BTL10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | FALSE
496 | Tauhara B Steamfield | TH26 110VDC System - Current Battery Systems | 10CE201 | Indication | ? | C | FALSE | FALSE | - | 0 to 150 A | TH26 110VDC System - Current - - | -edit- | 0 to 150 A | +/- 1% | TH000260BTL10CE201 | - |  | - |  | Amps | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
497 | Tauhara B Steamfield | TH28 110VDC System - Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 150 V | TH28 110VDC System - Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH000280BTL10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | FALSE
498 | Tauhara B Steamfield | TH28 110VDC System - Current Battery Systems | 10CE201 | Indication | ? | C | FALSE | FALSE | - | 0 to 150 A | TH28 110VDC System - Current - - | -edit- | 0 to 150 A | +/- 1% | TH000280BTL10CE201 | - |  | - |  | Amps | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
499 | Tauhara B Steamfield | TH29 110VDC System - Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 150 V | TH29 110VDC System - Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH000290BTL10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | FALSE
500 | Tauhara B Steamfield | TH29 110VDC System - Current Battery Systems | 10CE201 | Indication | ? | C | FALSE | FALSE | - | 0 to 150 A | TH29 110VDC System - Current - - | -edit- | 0 to 150 A | +/- 1% | TH000290BTL10CE201 | - |  | - |  | Amps | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
501 | Tauhara B Steamfield | TH37 110VDC System - Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 150 V | TH37 110VDC System - Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH000370BTL10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | FALSE
502 | Tauhara B Steamfield | TH37 110VDC System - Current Battery Systems | 10CE201 | Indication | ? | C | FALSE | FALSE | - | 0 to 150 A | TH37 110VDC System - Current - - | -edit- | 0 to 150 A | +/- 1% | TH000370BTL10CE201 | - |  | - |  | Amps | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
503 | Tauhara B Steamfield | SGW 230VAC Inverter A Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 300 V | SGW 230VAC Inverter A Output Voltage - - | -edit- | 0 to 300 V | +/- 1% | TH00P020BRA10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 75 | 150 | 225 | 300 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 215 | [5 empty] | FALSE
504 | Tauhara B Steamfield | SGW 230VAC Inverter A Output Current Battery Systems | 10CE201 | Indication | ? | C | FALSE | FALSE | - | 0 to 40 A | SGW 230VAC Inverter A Output Current - - | -edit- | 0 to 40 A | +/- 1% | TH00P020BRA10CE201 | - |  | - |  | Amps | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 10 | 20 | 30 | 40 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
505 | Tauhara B Steamfield | SGW 230VAC Inverter B Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 300 V | SGW 230VAC Inverter B Output Voltage - - | -edit- | 0 to 300 V | +/- 1% | TH00P020BRB10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 75 | 150 | 225 | 300 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 215 | [5 empty] | FALSE
506 | Tauhara B Steamfield | SGW 230VAC Inverter B Output Current Battery Systems | 10CE201 | Indication | ? | C | FALSE | FALSE | - | 0 to 40 A | SGW 230VAC Inverter B Output Current - - | -edit- | 0 to 40 A | +/- 1% | TH00P020BRB10CE201 | - |  | - |  | Amps | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 10 | 20 | 30 | 40 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
507 | Tauhara B Steamfield | SGW 110VDC System A Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 150 V | SGW 110VDC System A Output Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH00P020BTL10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | FALSE
508 | Tauhara B Steamfield | SGW 110VDC System A Output current Battery Systems | 10CE201 | Indication | ? | C | FALSE | FALSE | - | 0 to 150 A | SGW 110VDC System A Output current - - | -edit- | 0 to 150 A | +/- 1% | TH00P020BTL10CE201 | - |  | - |  | Amps | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
509 | Tauhara B Steamfield | SGW 110VDC System B Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 150 V | SGW 110VDC System B Output Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH00P020BTM10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | FALSE
510 | Tauhara B Steamfield | SGW 110VDC System B Output current Battery Systems | 10CE201 | Indication | ? | C | FALSE | FALSE | - | 0 to 100A | SGW 110VDC System B Output current - - | -edit- | 0 to 100A | +/- 1% | TH00P020BTM10CE201 | - |  | - |  | Amps | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
511 | Tauhara B Steamfield | SP 230VAC Inverter A Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 300 V | SP 230VAC Inverter A Output Voltage - - | -edit- | 0 to 300 V | +/- 1% | TH00S020BRA10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 75 | 150 | 225 | 300 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 215 | [5 empty] | FALSE
512 | Tauhara B Steamfield | SP 230VAC Inverter B Output Voltage Battery Systems | 10CE201 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 300 V | SP 230VAC Inverter B Output Voltage - - | -edit- | 0 to 300 V | +/- 1% | TH00S020BRA10CE201 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 75 | 150 | 225 | 300 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 215 | [5 empty] | FALSE
513 | Tauhara B Steamfield | SP 110VDC System A Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 150 V | SP 110VDC System A Output Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH00S020BTL10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | FALSE
514 | Tauhara B Steamfield | SP 110VDC System B Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 150 V | SP 110VDC System B Output Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH00S020BTM10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | FALSE
515 | Tauhara B Steamfield | SP 230VAC Inverter B Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 300 V | SP 230VAC Inverter B Output Voltage - - | -edit- | 0 to 300 V | +/- 1% | TH00S020BRB10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 75 | 150 | 225 | 300 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
516 | Tauhara B Steamfield | PLC Cabinet TH11 24Vdc Comms DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TH11 24Vdc Comms - - | -edit- | 0 to 50 VDC | +/- 1% | TH000110CRA10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
517 | Tauhara B Steamfield | PLC Cabinet TH11 24Vdc IO DCS Power Supplies | 10CE102 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TH11 24Vdc IO - - | -edit- | 0 to 50 VDC | +/- 1% | TH000110CRA10CE102 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
518 | Tauhara B Steamfield | PLC Cabinet TH12 24Vdc Comms DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TH12 24Vdc Comms - - | -edit- | 0 to 50 VDC | +/- 1% | TH000120CRA10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
519 | Tauhara B Steamfield | PLC Cabinet TH12 24Vdc IO DCS Power Supplies | 10CE102 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TH12 24Vdc IO - - | -edit- | 0 to 50 VDC | +/- 1% | TH000120CRA10CE102 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
520 | Tauhara B Steamfield | PLC Cabinet TH26 24Vdc Comms DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TH26 24Vdc Comms - - | -edit- | 0 to 50 VDC | +/- 1% | TH000260CRA10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
521 | Tauhara B Steamfield | PLC Cabinet TH26 24Vdc IO DCS Power Supplies | 10CE201 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TH26 24Vdc IO - - | -edit- | 0 to 50 VDC | +/- 1% | TH000260CRA10CE201 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
522 | Tauhara B Steamfield | PLC Cabinet TH28 24Vdc Comms DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TH28 24Vdc Comms - - | -edit- | 0 to 50 VDC | +/- 1% | TH000280CRA10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
523 | Tauhara B Steamfield | PLC Cabinet TH28 24Vdc IO DCS Power Supplies | 10CE201 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TH28 24Vdc IO - - | -edit- | 0 to 50 VDC | +/- 1% | TH000280CRA10CE201 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
524 | Tauhara B Steamfield | PLC Cabinet TH29 24Vdc Comms DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TH29 24Vdc Comms - - | -edit- | 0 to 50 VDC | +/- 1% | TH000290CRA10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
525 | Tauhara B Steamfield | PLC Cabinet TH29 24Vdc IO DCS Power Supplies | 10CE201 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TH29 24Vdc IO - - | -edit- | 0 to 50 VDC | +/- 1% | TH000290CRA10CE201 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
526 | Tauhara B Steamfield | PLC Cabinet TH37 24Vdc Comms DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TH37 24Vdc Comms - - | -edit- | 0 to 50 VDC | +/- 1% | TH000370CRA10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
527 | Tauhara B Steamfield | PLC Cabinet TH37 24Vdc IO DCS Power Supplies | 10CE201 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TH37 24Vdc IO - - | -edit- | 0 to 50 VDC | +/- 1% | TH000370CRA10CE201 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
528 | Tauhara B Steamfield | PLC Cabinet TAS3 24Vdc DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TAS3 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
529 | Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 1 24Vdc DCS Power Supplies | 10CE102 | Alarm & Indication | ? | C | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TAS3 Cluster 1 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE102 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
530 | Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 2 24Vdc DCS Power Supplies | 10CE103 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TAS3 Cluster 2 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE103 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
531 | Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 3 24Vdc DCS Power Supplies | 10CE104 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TAS3 Cluster 3 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE104 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
532 | Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 4 24Vdc DCS Power Supplies | 10CE105 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TAS3 Cluster 4 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE105 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
533 | Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 5 24Vdc DCS Power Supplies | 10CE106 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TAS3 Cluster 5 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE106 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
534 | Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 6 24Vdc DCS Power Supplies | 10CE107 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TAS3 Cluster 6 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE107 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
535 | Tauhara B Steamfield | PLC Cabinet TAS3 Vibration Rack 24Vdc DCS Power Supplies | 10CE109 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TAS3 Vibration Rack 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE109 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
536 | Tauhara B Steamfield | Server Cabinet NSP 24Vdc DCS Power Supplies | 10CE101 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | Server Cabinet NSP 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRS10CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
537 | Tauhara B Steamfield | Server Cabinet BLDG Services 24Vdc DCS Power Supplies | 10CE102 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | Server Cabinet BLDG Services 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRS10CE102 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
538 | Tauhara B Steamfield | PLC Cabinet TAS1 24Vdc DCS Power Supplies | 20CE101 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TAS1 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00S020CRA20CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
539 | Tauhara B Steamfield | PLC Cabinet TAS2 24Vdc DCS Power Supplies | 30CE101 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TAS2 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00S020CRA30CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
540 | Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 1 24Vdc DCS Power Supplies | 30CE102 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | PLC Cabinet TAS2 Cluster 1 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00S020CRA30CE102 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
541 | Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 2 24Vdc DCS Power Supplies | 30CE103 | Alarm & Indication | ? | - | FALSE | FALSE | - | - | PLC Cabinet TAS2 Cluster 2 24Vdc - - | -edit- | - | +/- 1% | TH00S020CRA30CE103 | - |  | - |  | - | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | FALSE
542 | Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 3 24Vdc DCS Power Supplies | 30CE104 | Alarm & Indication | ? | - | FALSE | FALSE | - | - | PLC Cabinet TAS2 Cluster 3 24Vdc - - | -edit- | - | +/- 1% | TH00S020CRA30CE104 | - |  | - |  | - | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | FALSE
543 | Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 4 24Vdc DCS Power Supplies | 30CE105 | Alarm & Indication | ? | - | FALSE | FALSE | - | - | PLC Cabinet TAS2 Cluster 4 24Vdc - - | -edit- | - | +/- 1% | TH00S020CRA30CE105 | - |  | - |  | - | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | FALSE
544 | Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 5 24Vdc DCS Power Supplies | 30CE106 | Alarm & Indication | ? | - | FALSE | FALSE | - | - | PLC Cabinet TAS2 Cluster 5 24Vdc - - | -edit- | - | +/- 1% | TH00S020CRA30CE106 | - |  | - |  | - | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | FALSE
545 | Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 6 24Vdc DCS Power Supplies | 30CE107 | Alarm & Indication | ? | - | FALSE | FALSE | - | - | PLC Cabinet TAS2 Cluster 6 24Vdc - - | -edit- | - | +/- 1% | TH00S020CRA30CE107 | - |  | - |  | - | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | FALSE
546 | Tauhara B Steamfield | Server Cabinet NSP 24Vdc DCS Power Supplies | 20CE101 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | Server Cabinet NSP 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00S020CRS20CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
547 | Tauhara B Steamfield | Server Cabinet Build Services 24Vdc DCS Power Supplies | 40CE101 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 VDC | Server Cabinet Build Services 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00S020CRS40CE101 | - |  | - |  | Volts | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
548 | Tauhara B Steamfield | Wellpad TH28 Common Steam/Water Dump | 10CP010 | Alarm & Indication | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 0 | -1 to 10.3 | Wellpad TH28 - Pressure | -edit- | 0 to 10 | +/- 1% | TH000280LFC10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-31 | rev: 3.7 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # 0280LFC10-BR532-350-CL1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
549 | Tauhara B Steamfield | Wellpad LCP (LCP2-1) Separated Water | 10CP501 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad LCP (LCP2-1) - Pressure | -edit- | - | +/- 1% | TH000320NDB10CP501 | CCI-DAT-1460 |  | PRO-PID-38 |  | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
550 | Tauhara B Steamfield | Wellpad LCP (LCP2-1) Separated Water | 10CP520 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad LCP (LCP2-1) - Pressure | -edit- | - | +/- 1% | TH000320NDB10CP520 | CCI-DAT-1460 |  | PRO-PID-38 |  | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
551 | Tauhara B Steamfield | Wellpad LCP (LCP2-2) Separated Water | 10CP510 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad LCP (LCP2-2) - Pressure | -edit- | - | +/- 1% | TH000330NDB10CP510 | CCI-DAT-1460 |  | PRO-PID-38 |  | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
552 | Tauhara B Steamfield | Wellpad LCP (LCP2-2) Separated Water | 10CP520 | - | Wika 72039876+14503369+0731277 | - | FALSE | FALSE | 15 | 0 to 60 | Wellpad LCP (LCP2-2) - Pressure | -edit- | - | +/- 1% | TH000330NDB10CP520 | CCI-DAT-1460 |  | PRO-PID-38 |  | bar(g) | bar(g) | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | FALSE
553 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping | 10-CT510 | - | Wika 72039934+72039931 | - | FALSE | FALSE | 215 | 0 to 250 | TH26 Two Phase Pipeline - - | -edit- | - | +/- 1% | TH00L070NDA10-CT510 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 instment type: Temperature Indicator (Gauge) make: Wika Vendor: Wika drwg: CCI-DET-2703 line # L070NDA10-BR030-750-CH1 | °C | °C | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 62.5 | 125 | 187.5 | 250 |  | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | FALSE
554 | Tauhara B Steamfield | SWG Pipeline to TH29 Wellpad Separated Water | 10CP011 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 15 | -1 to 55 | SWG Pipeline to TH29 Wellpad - - | -edit- | 0 to 50 | +/- 1% | TH00L210NDB10CP011 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-32 | rev: 5.6 instment type: Pressure Indicating Transmitter make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 line # L190NDB10-BR002-500-CR1 | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
555 | Tauhara B Steamfield | Wellpad LCP Common Steam/Water Dump | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | FALSE | FALSE | - | 0 to 6000 | Wellpad LCP - - | -edit- | 0 to 6000 | +/- 1% | TH00LCP0LFC10CL010 | CCI-DAT-1468 |  | PRO-PID-38 |  | mm | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 1500 | 3000 | 4500 | 6000 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
556 | Tauhara B Steamfield | Pump Station Raw Water | 20CP020 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | FALSE | FALSE | 3.49 | 0 to 25 | Pump Station - - | -edit- | - | +/- 1% | TH00S020GAC20CP020 | CCI-DAT-1460 |  | PRO-PID-51 |  | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
557 | Tauhara B Steamfield | Separation Plant Production Piping | 20CR004 | - | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - | FALSE | FALSE | * | * | Separation Plant - - | -edit- | * | +/- 1% | TH00S020NDA20CR004 | COSASCO Model 3500/3500HT ER-420 |  | PRO-PID-14 |  | mm/Time Unit | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 0 | 0 | 0 | 0 |  | - | - | - | - | - | [9 empty] | FALSE
558 | Tauhara B Steamfield | TH11 Building Temp Building Services | 10CT010 | - | RTD PT100 | - | FALSE | FALSE | - | 0 to 100 | TH11 Building Temp - - | -edit- | - | +/- 1% | TH000110SAA10CT010 | - |  | - |  | deg C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
559 | Tauhara B Steamfield | TH12 Building Temp Building Services | 10CT010 | - | RTD PT100 | - | FALSE | FALSE | - | 0 to 100 | TH12 Building Temp - - | -edit- | - | +/- 1% | TH000120SAA10CT010 | - |  | - |  | deg C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
560 | Tauhara B Steamfield | TH26 Building Temp Building Services | 10CT010 | - | RTD PT100 | - | FALSE | FALSE | - | 0 to 100 | TH26 Building Temp - - | -edit- | - | +/- 1% | TH000260SAA10CT010 | - |  | - |  | deg C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
561 | Tauhara B Steamfield | TH28 Building Temp Building Services | 10CT010 | - | RTD PT100 | - | FALSE | FALSE | - | 0 to 100 | TH28 Building Temp - - | -edit- | - | +/- 1% | TH000280SAA10CT010 | - |  | - |  | deg C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
562 | Tauhara B Steamfield | TH29 Building Temp Building Services | 10CT010 | - | RTD PT100 | - | FALSE | FALSE | - | 0 to 100 | TH29 Building Temp - - | -edit- | - | +/- 1% | TH000290SAA10CT010 | - |  | - |  | deg C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
563 | Tauhara B Steamfield | TH37 Building Temp Building Services | 10CT010 | - | RTD PT100 | - | FALSE | FALSE | - | 0 to 100 | TH37 Building Temp - - | -edit- | - | +/- 1% | TH000370SAA10CT010 | - |  | - |  | deg C | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
564 | Tauhara B Steamfield | SIS PLC Cabinet TAS4 24Vdc System DCS Power Supplies | 40CE101 | Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 50 | SIS PLC Cabinet TAS4 24Vdc System - - | -edit- | - | +/- 1% | TH00S020CRJ40CE101 | - |  | - |  | V | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | FALSE
565 | Tauhara B Steamfield | SIS PLC Cabinet TAS4 Cluster 24VDC DCS Power Supplies | 40CE102 | - | ? | - | FALSE | FALSE | - | 0 to 50 | SIS PLC Cabinet TAS4 Cluster 24VDC - - | -edit- | - | +/- 1% | TH00S020CRJ40CE102 | - |  | - |  | V | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | FALSE
566 | Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CF010 | Trip & Alarm & Indication | ? | - | FALSE | FALSE | - | 0 to 10 | Separation Plant - - | -edit- | 0 to 10 | +/- 1% | TH00S020GWA11CF010 | - | PO# Vendor Supplied | TABG-JEC-0-000-PRO-PID-0055 | rev: 4.9 instment type: Flow Transmitter (Magnetic) make: Vendor Supplied Vendor: Vendor Supplied drwg: line # | l/m | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 2.5 | 5 | 7.5 | 10 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | FALSE
567 | Tauhara B Steamfield | Acid Dosing Seal Water Flushing Circuit B Flow Acid Dosing Seal Water | 10CF020 | Trip & Alarm & Indication | ? | - | FALSE | FALSE | - | Vendor supplied | Acid Dosing Seal Water Flushing Circuit B Flow - - | -edit- | - | +/- 1% | TH00S020GWA11CF020 | - | PO# Vendor Supplied | TABG-JEC-0-000-PRO-PID-0055 | rev: 4.9 instment type: Flow Transmitter (Magnetic) make: Vendor Supplied Vendor: Vendor Supplied drwg: line # | - | - | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | - | - | - | - | - |  | - | - | - | - | - |  |  |  | 8.5 | 8.7 |  | 7 |  |  | FALSE
568 | Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CP011 | - | ? | - | FALSE | FALSE | - | 0 to 25 | Separation Plant - - | -edit- | 0 to 25 | +/- 1% | TH00S020GWA10CP011 | - |  | TABG-JEC-0-000-PRO-PID-0055 |  | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
569 | Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CP012 | - | ? | - | FALSE | FALSE | - | 0 to 25 | Separation Plant - - | -edit- | 0 to 25 | +/- 1% | TH00S020GWA10CP012 | - |  | TABG-JEC-0-000-PRO-PID-0055 |  | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
570 | Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CP021 | - | ? | - | FALSE | FALSE | - | 0 to 25 | Separation Plant - - | -edit- | 0 to 25 | +/- 1% | TH00S020GWA10CP021 | - |  | TABG-JEC-0-000-PRO-PID-0055 |  | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE
571 | Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CP022 | - | ? | - | FALSE | FALSE | - | 0 to 25 | Separation Plant - - | -edit- | 0 to 25 | +/- 1% | TH00S020GWA10CP022 | - |  | TABG-JEC-0-000-PRO-PID-0055 |  | bar(g) | mA | FALSE | 2024-01-22 | RF & MduP | FALSE | FALSE | 0 | 6.25 | 12.5 | 18.75 | 25 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | FALSE