## Sheet1
| Station | System | Tag | Funct | Type | Criticality | ResCon | PECPR | NominalValue | Range | Point | DeviceType | Setting | Proof | PlantCode | Data (CCI-DAT-) | StoresNo | DrawingNo | Procs | MVUnit | IdealUnit | Checked | DateChecked | CheckedBy | Changed | CalcErr | MVar1 | MVar2 | MVar3 | MVar4 | MVar5 | MVar6 | IdO1 | IdO2 | IdO3 | IdO4 | IdO5 | IdO6 | MVar7 | IdO7 | Digi1 | Digi2 | Digi3 | Digi4 | Digi5 | Digi6 | KPI | DigiAliase1 | DigiAliase2 | DigiAliase3 | DigiAliase4 | DigiAliase5 | DigiAliase6
0 | Tauhara B Steamfield | Wellpad TH11 Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | C | NO | NO | - | 2200 to 6000 | Wellpad TH11 - Level | -edit- | 2200 to 6000 | +/- 1% | TH000110LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-33 | rev: 7.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 2200 | 3150 | 4100 | 5050 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | NO
1 | Tauhara B Steamfield | Wellpad TH11 Condensate System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B | NO | NO | 550 | -10 to 1500 | Wellpad TH11 - Flow | -edit- | 0 to 1500 | +/- 1% | TH000110NAB10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-33 | rev: 7.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 375 | 750 | 1125 | 1500 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
2 | Tauhara B Steamfield | Wellpad TH11 Condensate System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B | NO | NO | 5.1 | -1 to 55 | Wellpad TH11 - Pressure | -edit- | 0 to 25 | +/- 1% | TH000110NAB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-33 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 20 | [5 empty] | NO
3 | Tauhara B Steamfield | Wellpad TH11 Condensate System | 10CP510 | - | Wika 72039878+14503369+0731277 | C | NO | NO | 5.1 | 0 to 25 | Wellpad TH11 - Pressure | -edit- | - | +/- 1% | TH000110NAB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-33 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | NO
4 | Tauhara B Steamfield | Wellpad TH11 Condensate System | 10CP520 | - | Wika 72039878+14503369+0731277 | C | NO | NO | 5.1 | 0 to 25 | Wellpad TH11 - Pressure | -edit- | - | +/- 1% | TH000110NAB10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-33 | rev: 7.3 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | NO
5 | Tauhara B Steamfield | Wellpad TH12 Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | C | NO | NO | 950 | 0 to 1300 | Wellpad TH12 - Level | -edit- | 0 to 1300 | +/- 1% | TH000120LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-37 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: (LFC-)MEC-AGT-2099 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 325 | 650 | 975 | 1300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
6 | Tauhara B Steamfield | Wellpad TH12 Common Steam/Water Dump System | 10CL020 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | NO | NO | 2350 | 2200 to 6000 | Wellpad TH12 - Level | -edit- | 2200 to 6000 | +/- 1% | TH000120LFC10CL020 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-37 | rev: 7.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 2200 | 3150 | 4100 | 5050 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | NO
7 | Tauhara B Steamfield | Wellpad TH12 Common Steam/Water Dump System | 10CP010 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | C | NO | NO | 0 | -1 to 10.3 | Wellpad TH12 - Pressure | -edit- | 0 to 10 | +/- 1% | TH000120LFC10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-37 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
8 | Tauhara B Steamfield | Wellpad TH12 Common Steam/Water Dump System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 30 | 0 to 100 | Wellpad TH12 - Pressure | -edit- | - | +/- 1% | TH000120LFC10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-37 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
9 | Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CF010 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B | NO | NO | 699 | TBC | Wellpad TH12 - Flow | -edit- | TBC | +/- 1% | TH000120NDA10CF010 | CCI-DAT-1472 Note 2 | PO# 4500191995 | PRO-PID-37 | rev: 6.3 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph (Note 1) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 192.5 | 385 | 577.5 | 770 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
10 | Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CP010 | - | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B | NO | NO | 0 | -1 to 276 | Wellpad TH12 - Pressure | -edit- | 0 to 75 | +/- 1% | TH000120NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-37 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 18.75 | 37.5 | 56.25 | 75 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | [5 empty] | NO
11 | Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CP510 | - | Wika 72039884+14503369+0763349 | C | NO | NO | 30 | 0 to 100 | Wellpad TH12 - Pressure | -edit- | - | +/- 1% | TH000120NDA10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-37 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
12 | Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CP520 | - | Wika 72039884+14503369+0763349 | C | NO | NO | 30 | 0 to 100 | Wellpad TH12 - Pressure | -edit- | - | +/- 1% | TH000120NDA10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-37 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
13 | Tauhara B Steamfield | Wellpad TH12 Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | C | NO | NO | 235 | 0 to 300 | Wellpad TH12 - Temperature | -edit- | 0 to 300 | +/- 1% | TH000120NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-37 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 75 | 150 | 225 | 300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
14 | Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CF010 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B | NO | NO | 699 | TBC | Wellpad TH12 (TH21) - Flow | -edit- | TBC | +/- 1% | TH000210NDA10CF010 | CCI-DAT-1472 Note 2 | PO# 4500191995 | PRO-PID-37 | rev: 6.3 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph (Note 1) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 192.5 | 385 | 577.5 | 770 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
15 | Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CP010 | - | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B | NO | NO | 30 | -1 to 276 | Wellpad TH12 (TH21) - Pressure | -edit- | 0 to 75 | +/- 1% | TH000210NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-37 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 18.75 | 37.5 | 56.25 | 75 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | [5 empty] | NO
16 | Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 30 | 0 to 100 | Wellpad TH12 (TH21) - Pressure | -edit- | - | +/- 1% | TH000210NDA10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-37 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
17 | Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CP520 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 30 | 0 to 100 | Wellpad TH12 (TH21) - Pressure | -edit- | - | +/- 1% | TH000210NDA10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-37 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
18 | Tauhara B Steamfield | Wellpad TH12 (TH21) Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 235 | 0 to 300 | Wellpad TH12 (TH21) - Temperature | -edit- | 0 to 300 | +/- 1% | TH000210NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-37 | rev: 4.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 75 | 150 | 225 | 300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
19 | Tauhara B Steamfield | Wellpad TH26 Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | NO | NO | 950 | 0 to 1300 | Wellpad TH26 - Level | -edit- | 0 to 1300 | +/- 1% | TH000260LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-36 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: (LFC-)MEC-AGT-2099 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 325 | 650 | 975 | 1300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
20 | Tauhara B Steamfield | Wellpad TH26 Common Steam/Water Dump System | 10CL020 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | NO | NO | 2350 | 2200 to 6000 | Wellpad TH26 - Level | -edit- | 2200 to 6000 | +/- 1% | TH000260LFC10CL020 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-36 | rev: 7.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 2200 | 3150 | 4100 | 5050 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | NO
21 | Tauhara B Steamfield | Wellpad TH26 Common Steam/Water Dump System | 10CP010 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 0 | -1 to 10.3 | Wellpad TH26 - Pressure | -edit- | 0 to 10 | +/- 1% | TH000260LFC10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-36 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
22 | Tauhara B Steamfield | Wellpad TH26 Common Steam/Water Dump System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 30 | 0 to 100 | Wellpad TH26 - Pressure | -edit- | - | +/- 1% | TH000260LFC10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-36 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
23 | Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CF010 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B | NO | NO | 699 | TBC | Wellpad TH26 - Flow | -edit- | TBC | +/- 1% | TH000260NDA10CF010 | CCI-DAT-1472 Note 2 | PO# 4500191995 | PRO-PID-36 | rev: 6.3 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph (Note 1) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 192.5 | 385 | 577.5 | 770 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
24 | Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CP010 | - | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B | NO | NO | 0 | -1 to 276 | Wellpad TH26 - Pressure | -edit- | 0 to 75 | +/- 1% | TH000260NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-36 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 18.75 | 37.5 | 56.25 | 75 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | [5 empty] | NO
25 | Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 30 | 0 to 100 | Wellpad TH26 - Pressure | -edit- | - | +/- 1% | TH000260NDA10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-36 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
26 | Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CP520 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 30 | 0 to 100 | Wellpad TH26 - Pressure | -edit- | - | +/- 1% | TH000260NDA10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-36 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
27 | Tauhara B Steamfield | Wellpad TH26 Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 235 | 0 to 300 | Wellpad TH26 - Temperature | -edit- | 0 to 300 | +/- 1% | TH000260NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-36 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 75 | 150 | 225 | 300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
28 | Tauhara B Steamfield | Wellpad TH28 Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | NO | NO | 950 | 0 to 1300 | Wellpad TH28 - Level | -edit- | 0 to 1300 | +/- 1% | TH000280LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-31 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: (LFC-)MEC-AGT-2099 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 325 | 650 | 975 | 1300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
29 | Tauhara B Steamfield | Wellpad TH28 Common Steam/Water Dump System | 10CL020 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | NO | NO | 2350 | 2200 to 6000 | Wellpad TH28 - Level | -edit- | 2200 to 6000 | +/- 1% | TH000280LFC10CL020 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-31 | rev: 7.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 2200 | 3150 | 4100 | 5050 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | NO
30 | Tauhara B Steamfield | Wellpad TH28 Common Steam/Water Dump System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 30 | 0 to 100 | Wellpad TH28 - Pressure | -edit- | - | +/- 1% | TH000280LFC10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-31 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
31 | Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CF010 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B | NO | NO | 531 | TBC | Wellpad TH28 - Flow | -edit- | TBC | +/- 1% | TH000280NDA10CF010 | CCI-DAT-1472 Note 2 | PO# 4500191995 | PRO-PID-31 | rev: 6.3 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | - | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | NO
32 | Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CP010 | - | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B | NO | NO | 26.3 | -1 to 276 | Wellpad TH28 - Pressure | -edit- | 0 to 75 | +/- 1% | TH000280NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-31 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 18.75 | 37.5 | 56.25 | 75 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | [5 empty] | NO
33 | Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 26.3 | 0 to 100 | Wellpad TH28 - Pressure | -edit- | - | +/- 1% | TH000280NDA10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-31 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
34 | Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CP520 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 20.5 | 0 to 100 | Wellpad TH28 - Pressure | -edit- | - | +/- 1% | TH000280NDA10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-31 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
35 | Tauhara B Steamfield | Wellpad TH28 Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 216 | 0 to 300 | Wellpad TH28 - Temperature | -edit- | 0 to 300 | +/- 1% | TH000280NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-31 | rev: 4.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 75 | 150 | 225 | 300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
36 | Tauhara B Steamfield | Wellpad TH29 Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | NO | NO | - | 2200 to 6000 | Wellpad TH29 - Level | -edit- | 2200 to 6000 | +/- 1% | TH000290LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-32 | rev: 7.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 2200 | 3150 | 4100 | 5050 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | NO
37 | Tauhara B Steamfield | Wellpad TH29 Separated Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 550 | -5 to 605 | Wellpad TH29 - Flow | -edit- | 0 to 900 | +/- 1% | TH000290NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-32 | rev: 7.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - | -5 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
38 | Tauhara B Steamfield | Wellpad TH29 Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 15 | -1 to 55 | Wellpad TH29 - Pressure | -edit- | 0 to 50 | +/- 1% | TH000290NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-32 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
39 | Tauhara B Steamfield | Wellpad TH29 Separated Water System | 10CP510 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad TH29 - Pressure | -edit- | - | +/- 1% | TH000290NDB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
40 | Tauhara B Steamfield | Wellpad TH29 Separated Water System | 10CP520 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad TH29 - Pressure | -edit- | - | +/- 1% | TH000290NDB10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
41 | Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CF010 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B | NO | NO | 699 | TBC | Wellpad TH26 (TH30) - Flow | -edit- | TBC | +/- 1% | TH000300NDA10CF010 | CCI-DAT-1472 Note 2 | PO# 4500191995 | PRO-PID-36 | rev: 6.3 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph (Note 1) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 192.5 | 385 | 577.5 | 770 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
42 | Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CP010 | - | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | B | NO | NO | 30 | -1 to 276 | Wellpad TH26 (TH30) - Pressure | -edit- | 0 to 75 | +/- 1% | TH000300NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-36 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 18.75 | 37.5 | 56.25 | 75 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | [5 empty] | NO
43 | Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 30 | 0 to 100 | Wellpad TH26 (TH30) - Pressure | -edit- | - | +/- 1% | TH000300NDA10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-36 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
44 | Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CP520 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 30 | 0 to 100 | Wellpad TH26 (TH30) - Pressure | -edit- | - | +/- 1% | TH000300NDA10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-36 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
45 | Tauhara B Steamfield | Wellpad TH26 (TH30) Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 235 | 0 to 300 | Wellpad TH26 (TH30) - Temperature | -edit- | 0 to 300 | +/- 1% | TH000300NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-36 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 75 | 150 | 225 | 300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
46 | Tauhara B Steamfield | Wellpad TH29 (TH31) Separated Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B | NO | NO | 550 | -5 to 605 | Wellpad TH29 (TH31) - Flow | -edit- | 0 to 1400 | +/- 1% | TH000310NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-32 | rev: 7.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 100 | 200 | 300 | 400 | -5 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
47 | Tauhara B Steamfield | Wellpad TH29 (TH31) Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B | NO | NO | 15 | -1 to 55 | Wellpad TH29 (TH31) - Pressure | -edit- | 0 to 50 | +/- 1% | TH000310NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-32 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 45 | [5 empty] | NO
48 | Tauhara B Steamfield | Wellpad TH29 (TH31) Separated Water System | 10CP501 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad TH29 (TH31) - Pressure | -edit- | - | +/- 1% | TH000310NDB10CP501 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
49 | Tauhara B Steamfield | Wellpad TH29 (TH31) Separated Water System | 10CP520 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad TH29 (TH31) - Pressure | -edit- | - | +/- 1% | TH000310NDB10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
50 | Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CF010 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | B | NO | NO | 531 | TBC | Wellpad TH28 (TH34) - Flow | -edit- | TBC | +/- 1% | TH000360NDA10CF010 | CCI-DAT-1472 Note 2 | PO# 4500191995 | PRO-PID-31 | rev: 6.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph (Note 1) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 147.5 | 295 | 442.5 | 590 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
51 | Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CF020 | - | Rosemount 3051SMV3M22G4N2A11A1BM5P1Q4Q8T1 | - | NO | NO | 531 | TBC | Wellpad TH28 (TH34) - Flow | -edit- | TBC | +/- 1% | TH000360NDA10CF020 | CCI-DAT-1472 Note 2 | PO# 4500193492 | PRO-PID-31 | rev: 6.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph (Note 1) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 147.5 | 295 | 442.5 | 590 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
52 | Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CP010 | - | Rosemount 2051TG4A2B21BS5B4M4Q4Q8 | - | NO | NO | 26.3 | -1 to 276 | Wellpad TH28 (TH34) - Pressure | -edit- | 0 to 75 | +/- 1% | TH000360NDA10CP010 |  | PO# 4500191995 | PRO-PID-31 | rev: 6.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 18.75 | 37.5 | 56.25 | 75 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | [5 empty] | NO
53 | Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CP510 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 26.3 | 0 to 100 | Wellpad TH28 (TH34) - Pressure | -edit- | - | +/- 1% | TH000360NDA10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-31 | rev: 6.4 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 |  | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
54 | Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CP520 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 20.5 | 0 to 100 | Wellpad TH28 (TH34) - Pressure | -edit- | - | +/- 1% | TH000360NDA10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-31 | rev: 6.4 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 |  | 0 | 25 | 50 | 75 | 100 | [9 empty] | NO
55 | Tauhara B Steamfield | Wellpad TH28 (TH34) Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 216 | 0 to 300 | Wellpad TH28 (TH34) - Temperature | -edit- | 0 to 300 | +/- 1% | TH000360NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-31 | rev: 6.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 75 | 150 | 225 | 300 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
56 | Tauhara B Steamfield | Wellpad TH29 (TH35) Separated Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B | NO | NO | 15 | -5 to 605 | Wellpad TH29 (TH35) - Flow | -edit- | -5 to 200 | +/- 1% | TH000350NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-32 | rev: 7.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -5 | 46.25 | 97.5 | 148.75 | 200 | -5 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
57 | Tauhara B Steamfield | Wellpad TH29 (TEA-3) Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B | NO | NO | 30 | -1 to 55 | Wellpad TH29 (TEA-3) - Pressure | -edit- | 0 to 50 | +/- 1% | TH000350NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-32 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 45 | [5 empty] | NO
58 | Tauhara B Steamfield | Wellpad TH29 (TH35) Separated Water System | 10CP510 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 30 | 0 to 60 | Wellpad TH29 (TH35) - Pressure | -edit- | - | +/- 1% | TH000350NDB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
59 | Tauhara B Steamfield | Wellpad TH29 (TH35) Separated Water System | 10CP520 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad TH29 (TH35) - Pressure | -edit- | - | +/- 1% | TH000350NDB10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
60 | Tauhara B Steamfield | Wellpad TH37 Separated Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B | NO | NO | 370 | 0 to 1000 | Wellpad TH37 - Flow | -edit- | 0 to 1000 | +/- 1% | TH000370NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-38 | rev: 7.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 250 | 500 | 750 | 1000 | -5 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
61 | Tauhara B Steamfield | Wellpad TH37 Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B | NO | NO | 15 | -1 to 55 | Wellpad TH37 - Pressure | -edit- | 0 to 50 | +/- 1% | TH000370NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-38 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 45 | [5 empty] | NO
62 | Tauhara B Steamfield | Wellpad TH37 Separated Water System | 10CP510 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad TH37 - Pressure | -edit- | - | +/- 1% | TH000370NDB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-38 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
63 | Tauhara B Steamfield | Wellpad TH37 Separated Water System | 10CP520 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad TH37 - Pressure | -edit- | - | +/- 1% | TH000370NDB10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-38 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
64 | Tauhara B Steamfield | Wellpad TH37/38 Separated Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | B | NO | NO | 370 | 0 to 1000 | Wellpad TH37/38 - Flow | -edit- | 0 to 1000 | +/- 1% | TH000380NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 |  | PRO-PID-38 |  | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 250 | 500 | 750 | 1000 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
65 | Tauhara B Steamfield | Wellpad TH37/38 Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | B | NO | NO | 15 | -1 to 55 | Wellpad TH37/38 - Pressure | -edit- | 0 to 50 | +/- 1% | TH000380NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-38 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 45 | [5 empty] | NO
66 | Tauhara B Steamfield | Wellpad TH37/38 Separated Water System | 10CP501 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad TH37/38 - Pressure | -edit- | - | +/- 1% | TH000380NDB10CP501 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-38 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
67 | Tauhara B Steamfield | Wellpad TH37/38 Separated Water System | 10CP520 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad TH37/38 - Pressure | -edit- | - | +/- 1% | TH000380NDB10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-38 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
68 | Tauhara B Steamfield | TH12 Two Phase Pipeline Production Piping System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 21.27 | -1 to 55 | TH12 Two Phase Pipeline - Pressure | -edit- | 0 to 35 | +/- 1% | TH00L050NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-11 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 8.75 | 17.5 | 26.25 | 35 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 20 | [5 empty] | NO
69 | Tauhara B Steamfield | TH12 Two Phase Pipeline Production Piping System | 10CP532 | - | Wika 72039883+14503369+0763349 | - | NO | NO | 25 | 0 to 40 | TH12 Two Phase Pipeline - Pressure | -edit- | - | +/- 1% | TH00L050NDA10CP532 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-37 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 10 | 20 | 30 | 40 | 0 | 0 | 10 | 20 | 30 | 40 | [9 empty] | NO
70 | Tauhara B Steamfield | TH12 Two Phase Pipeline Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 217.9 | 0 to 250 | TH12 Two Phase Pipeline - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L050NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-11 | rev: 4.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
71 | Tauhara B Steamfield | TH12 Two Phase Pipeline Production Piping System | 10CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 215 | 0 to 250 | TH12 Two Phase Pipeline - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L050NDA10CT030 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-37 | rev: 4.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
72 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 21.27 | -1 to 55 | TH28 Two Phase Pipeline - Pressure | -edit- | 0 to 35 | +/- 1% | TH00L060NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-11 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 8.75 | 17.5 | 26.25 | 35 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 20 | [5 empty] | NO
73 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CP532 | - | Wika 72039884+14503369+0763349 | - | NO | NO | 20.5 | -1 to 55 | TH28 Two Phase Pipeline - Pressure | -edit- | 0 to 50 | +/- 1% | TH00L060NDA10CP532 | CCI-DAT-1460 | PO# 4500195012 | PRO-PID-31 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 0 | 12.5 | 25 | 37.5 | 50 | [9 empty] | NO
74 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 217.9 | 0 to 250 | TH28 Two Phase Pipeline - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L060NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-11 | rev: 4.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
75 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 216 | 0 to 250 | TH28 Two Phase Pipeline - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L060NDA10CT030 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-31 | rev: 4.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
76 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT510 | - | Wika 72039934 (Model S5550/4) +72039931 (TW15-H) | - | NO | NO | 215 | 0 to 250 | TH28 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L060NDA10CT510 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
77 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT511 | - | Wika 72039935 Model S5550)+72039932 (Model TW15-H) | - | NO | NO | 215 | 0 to 250 | TH28 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L060NDA10CT511 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
78 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT520 | - | Wika 72039934 (Model S5550/4) +72039931 (TW15-H) | - | NO | NO | 215 | 0 to 250 | TH28 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L060NDA10CT520 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
79 | Tauhara B Steamfield | TH28 Two Phase Pipeline Production Piping System | 10CT521 | - | Wika 72040072 (Model S5550/4) +72040071 (TW15-H) | - | NO | NO | 215 | 0 to 250 | TH28 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L060NDA10CT521 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
80 | Tauhara B Steamfield | TH26 Two Phase Pipeline Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | NO | NO | - | 2200 to 6000 | TH26 Two Phase Pipeline - Level | -edit- | 2200 to 6000 | +/- 1% | TH00L070LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-34 | rev: 7.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 2200 | 3150 | 4100 | 5050 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | NO
81 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 21.27 | -1 to 55 | TH26 Two Phase Pipeline - Pressure | -edit- | 0 to 35 | +/- 1% | TH00L070NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-11 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 8.75 | 17.5 | 26.25 | 35 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 20 | [5 empty] | NO
82 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CP532 | - | Wika 72039883+14503369+0763349 | - | NO | NO | 25 | 0 to 40 | TH26 Two Phase Pipeline - Pressure | -edit- | - | +/- 1% | TH00L070NDA10CP532 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-36 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 10 | 20 | 30 | 40 | 0 | 0 | 10 | 20 | 30 | 40 | [9 empty] | NO
83 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 217.9 | 0 to 250 | TH26 Two Phase Pipeline - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L070NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-11 | rev: 4.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
84 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 215 | 0 to 250 | TH26 Two Phase Pipeline - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L070NDA10CT030 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-36 | rev: 4.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
85 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT510 | - | Wika 72039934 (Model S5550/4) +72039931 (TW15-H) | - | NO | NO | 215 | 0 to 250 | TH26 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L070NDA10CT510 | CCI-DAT-1463 |  | PRO-PID-34 |  | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
86 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT511 | - | Wika 72039934 (Model S5550/4) +72039931 (TW15-H) | - | NO | NO | 215 | 0 to 250 | TH26 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L070NDA10CT511 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
87 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT512 | - | Wika 72039935 Model S5550)+72039932 (Model TW15-H) | - | NO | NO | 215 | 0 to 250 | TH26 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L070NDA10CT512 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
88 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping System | 10CT522 | - | Wika 72040072 (Model S5550/4) +72040071 (TW15-H) | - | NO | NO | 215 | 0 to 250 | TH26 Two Phase Pipeline - Temperature | -edit- | - | +/- 1% | TH00L070NDA10CT522 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
89 | Tauhara B Steamfield | Condensate Pipeline To TH11 Condensate System | 10CP510 | - | Wika 72039879+14503369+0731277 | - | NO | NO | 5 | 0 to 16 | Condensate Pipeline To TH11 - Pressure | -edit- | - | +/- 1% | TH00L150NAB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-33 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 0 | 0 | 4 | 8 | 12 | 16 | [9 empty] | NO
90 | Tauhara B Steamfield | SGW Pipeline To TH29 Well Pad Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 30 | -1 to 55 | SGW Pipeline To TH29 Well Pad - Pressure | -edit- | -1 to 50 | +/- 1% | TH00L190NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-35 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -1 | 11.75 | 24.5 | 37.25 | 50 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
91 | Tauhara B Steamfield | SWG Pipeline to TH29 Wellpad Separated Water System | 10CP011 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 15 | -1 to 55 | SWG Pipeline to TH29 Wellpad - Pressure | -edit- | 0 to 50 | +/- 1% | TH00L190NDB10CP011 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-32 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
92 | Tauhara B Steamfield | SWG Pipeline to TH29 Wellpad Separated Water System | 10CP510 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | SWG Pipeline to TH29 Wellpad - Pressure | -edit- | - | +/- 1% | TH00L190NDB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-32 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
93 | Tauhara B Steamfield | SWG Pipeline to TH29 Wellpad Separated Water System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 123 | 0 to 250 | SWG Pipeline to TH29 Wellpad - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L190NDB10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-32 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
94 | Tauhara B Steamfield | SGW Pipeline To TH19N Separated Water System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 30 | -1 to 55 | SGW Pipeline To TH19N - Pressure | -edit- | -1 to 50 | +/- 1% | TH00L200NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-35 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -1 | 11.75 | 24.5 | 37.25 | 50 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
95 | Tauhara B Steamfield | SGW Pipeline To Wellpad LCP Separated Water System | 10CP510 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | SGW Pipeline To Wellpad LCP - Pressure | -edit- | - | +/- 1% | TH00L210NDB10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-38 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
96 | Tauhara B Steamfield | SGW Pipeline To Wellpad LCP Separated Water System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 123 | 0 to 250 | SGW Pipeline To Wellpad LCP - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L210NDB10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-38 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
97 | Tauhara B Steamfield | Wellpad TH37 Common Steam/Water Dump System | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | NO | NO | - | 2200 to 6000 | Wellpad TH37 - Level | -edit- | 2200 to 6000 | +/- 1% | TH000370LFC10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-38 | rev: 7.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 CCI-DET-2711 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 2200 | 3150 | 4100 | 5050 | 6000 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 500 | [5 empty] | NO
98 | Tauhara B Steamfield | Pump Station Seal Water System | 20CL010 | - | Rosemount 5408F1SHA2NA1R2ABCAA2M5DA1Q4Q8 | - | NO | NO |  | Note 9 | Pump Station - Level | -edit- | Note 9 | +/- 1% | TH00P020GWA20CL010 | CCI-DAT-1468 | PO# 4500191995 | PRO-PID-41 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2706 PRO-DAT-0078 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
99 | Tauhara B Steamfield | Pump Station Seal Water System | 20CL011 | - | Vendor Supplied Vendor Supplied | - | NO | NO |  | Note 9 | Pump Station - Level | -edit- | Refer to Notes | +/- 1% | TH00P020GWA20CL011 | CCI-DAT-1471 |  | PRO-PID-41 |  | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
100 | Tauhara B Steamfield | Pump Station Seal Water System | 20CL020 | - | Rosemount 5408F1SHA2NA1R2ABCAA2M5DA1Q4Q8 | - | NO | NO |  | Note 9 | Pump Station - Level | -edit- | Note 9 | +/- 1% | TH00P020GWA20CL020 | CCI-DAT-1468 | PO# 4500191995 | PRO-PID-41 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2706 PRO-DAT-0078 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
101 | Tauhara B Steamfield | Pump Station Seal Water System | 20CL021 | - | Vendor Supplied Vendor Supplied | - | NO | NO |  | Note 9 | Pump Station - Level | -edit- | Refer to Notes | +/- 1% | TH00P020GWA20CL021 | CCI-DAT-1471 |  | PRO-PID-41 |  | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
102 | Tauhara B Steamfield | Pump Station Potable Water System | 21CP520 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 3.49 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 10 | +/- 1% | TH00S020GKA21CP520 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-40 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2701 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 7.5 | [5 empty] | NO
103 | Tauhara B Steamfield | Pump Station Seal Water System | 20CP510 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA20CP510 | CCI-DAT-1460 |  | PRO-PID-41 |  | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
104 | Tauhara B Steamfield | Pump Station Seal Water System | 20CP511 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA20CP511 | CCI-DAT-1460 |  | PRO-PID-41 |  | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
105 | Tauhara B Steamfield | Pump Station Seal Water System | 30CP590 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA30CP590 | CCI-DAT-1460 |  | PRO-PID-41 |  | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
106 | Tauhara B Steamfield | Pump Station Seal Water System | 30CP591 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA30CP591 | CCI-DAT-1460 |  | PRO-PID-41 |  | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
107 | Tauhara B Steamfield | Pump Station Seal Water System | 30CT050 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 32 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020GWA30CT050 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-41 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 40 | [5 empty] | NO
108 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CL010 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | NO | NO | 773 | TBC | Pump Station - Level | -edit- | TBC | +/- 1% | TH00P020PCB20CL010 | CCI-DAT-1467 | PO# 4500191995 | PRO-PID-44 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
109 | Tauhara B Steamfield | Pump Station Seal Water System | 21CP001 | - | Rosemount 2051CD3A02A1BS5M4Q4 | - | NO | NO | 0 | -2500 to 2500 | Pump Station - Pressure | -edit- | 0 to 250mbar | +/- 1% | TH00P020GWA21CP001 | CCI-DAT-1462 | PO# 4500191995 | PRO-PID-42 | rev: 4.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | mbar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 200 |  | 50 |  |  |  | NO
110 | Tauhara B Steamfield | Pump Station Seal Water System | 21CP002 | - | Rosemount 2051TG1A2B21BS5B4M4Q4Q8 | - | NO | NO | -0.34 | -1 to 2.1 | Pump Station - Pressure | -edit- | -0.7 to +0.7 | +/- 1% | TH00P020GWA21CP002 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-42 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -0.7 | -0.35 | 0 | 0.35 | 0.7 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
111 | Tauhara B Steamfield | Pump Station Seal Water System | 22CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 c/w 0306RT22BA11++ | - | NO | NO | 11.77 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 15 | +/- 1% | TH00P020GWA22CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-42 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
112 | Tauhara B Steamfield | Pump Station Seal Water System | 22CP510 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA22CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-42 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
113 | Tauhara B Steamfield | Pump Station Seal Water System | 30CF010 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | NO | NO | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA30CF010 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | NO
114 | Tauhara B Steamfield | Pump Station Seal Water System | 30CF011 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | NO | NO | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA30CF011 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | NO
115 | Tauhara B Steamfield | Pump Station Seal Water System | 31CF020 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | NO | NO | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA31CF020 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | NO
116 | Tauhara B Steamfield | Pump Station Seal Water System | 30CF021 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | NO | NO | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA31CF021 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | NO
117 | Tauhara B Steamfield | Pump Station Seal Water System | 32CF030 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | NO | NO | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA32CF030 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | NO
118 | Tauhara B Steamfield | Pump Station Seal Water System | 32CF031 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | NO | NO | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA32CF031 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | NO
119 | Tauhara B Steamfield | Pump Station Seal Water System | 33CF040 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | NO | NO | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA33CF040 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 5.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  |  | 8.7 |  | 7 |  |  | NO
120 | Tauhara B Steamfield | Pump Station Seal Water System | 33CF041 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4+ | - | NO | NO | 8 | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWA33CF041 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-43 | rev: 7.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  |  | 8.7 |  | 7 |  |  | NO
121 | Tauhara B Steamfield | Pump Station Seal Water System | 30CP501 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA30CP501 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
122 | Tauhara B Steamfield | Pump Station Seal Water System | 30CP502 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA30CP502 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
123 | Tauhara B Steamfield | Pump Station Seal Water System | 30CP503 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA30CP503 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
124 | Tauhara B Steamfield | Pump Station Seal Water System | 30CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 32 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020GWA30CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-43 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 50 | [5 empty] | NO
125 | Tauhara B Steamfield | Pump Station Seal Water System | 31CT020 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 32 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020GWA31CT020 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-43 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 50 | [5 empty] | NO
126 | Tauhara B Steamfield | Pump Station Seal Water System | 32CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 32 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020GWA32CT030 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-43 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 50 | [5 empty] | NO
127 | Tauhara B Steamfield | Pump Station Seal Water System | 33CT040 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 32 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020GWA33CT040 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-43 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 50 | [5 empty] | NO
128 | Tauhara B Steamfield | Pump Station Seal Water System | 31CP511 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA31CP511 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
129 | Tauhara B Steamfield | Pump Station Seal Water System | 31CP512 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA31CP512 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
130 | Tauhara B Steamfield | Pump Station Seal Water System | 31CP513 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA31CP513 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
131 | Tauhara B Steamfield | Pump Station Seal Water System | 32CP521 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA32CP521 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
132 | Tauhara B Steamfield | Pump Station Seal Water System | 32CP522 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA32CP522 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
133 | Tauhara B Steamfield | Pump Station Seal Water System | 32CP523 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA32CP523 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
134 | Tauhara B Steamfield | Pump Station Seal Water System | 33CP531 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA33CP531 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
135 | Tauhara B Steamfield | Pump Station Seal Water System | 33CP532 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA33CP532 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
136 | Tauhara B Steamfield | Pump Station Seal Water System | 33CP533 | - | Wika 72039876+14503369+ | - | NO | NO | 11.77 | 0 to 15 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020GWA33CP533 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-43 | rev: 3.5 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | [9 empty] | NO
137 | Tauhara B Steamfield | Pump Station Seal Water System | 10CL010 | - | Vega PS21.XXXXXGMHB+GFL-PULS.GG | - | NO | NO |  | 0 to 3000 | Pump Station - Level | -edit- | 0 to 3000 | +/- 1% | TH00P020GWB10CL010 | CC-DAT-1468 | PO# 4500196238 | PRO-PID-56 | rev: 4.9 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 PRO-DAT-0078 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 750 | 1500 | 2250 | 3000 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
138 | Tauhara B Steamfield | Pump Station Seal Water System | 10CL011 | - | Vendor Supplied | - | NO | NO |  | 0 to 3000 | Pump Station - Level | -edit- | 0 to 3000 | +/- 1% | TH00P020GWB10CL011 |  | PO# Vendor Supplied | PRO-PID-56 | rev: 4.9 make: Vendor Supplied Vendor: Vendor Supplied drwg: | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 750 | 1500 | 2250 | 3000 | 0 | 0 | 750 | 1500 | 2250 | 3000 | [9 empty] | NO
139 | Tauhara B Steamfield | Pump Station Seal Water System | 10CP510 | - | Rosemount 2051CD3A02A1BS5M4Q4+0305RC52B11B4 | - | NO | NO | 1.7 | 0 to 2.5 | Pump Station - Pressure | -edit- | 0 to 2.5 | +/- 1% | TH00P020GWB10CP510 | CCI-DAT-1462 | PO# 4500197800 | PRO-PID-56 | rev: 5.9 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0.625 | 1.25 | 1.875 | 2.5 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
140 | Tauhara B Steamfield | Pump Station Seal Water System | 21CF010 | - | SM6020, SMR12GGX50KG/US-100 | - | NO | NO |  | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWB21CF010 | CCI-DAT-1474 | PO# 4500196549 | PRO-PID-56 | rev: 5.6 make: IFM Vendor: IFM drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
141 | Tauhara B Steamfield | Pump Station Seal Water System | 21CF020 | - | SM6020, SMR12GGX50KG/US-100 | - | NO | NO |  | 0 to 35 | Pump Station - Flow | -edit- | 0 to 35 | +/- 1% | TH00P020GWB21CF020 | CCI-DAT-1474 | PO# 4500196549 | PRO-PID-56 | rev: 5.6 make: IFM Vendor: IFM drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 8.75 | 17.5 | 26.25 | 35 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
142 | Tauhara B Steamfield | Pump Station Seal Water System | 21CP511 | - | Wika 72039878+14298395 | - | NO | NO | 13 | 0 to 25 | Pump Station - Pressure | -edit- | 0 to 25 | +/- 1% | TH00P020GWB21CP511 | CCI-DAT-1460 | PO# 4500197977 | PRO-PID-56 | rev: 5.8 make: Wika Vendor: Wika drwg: | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | NO
143 | Tauhara B Steamfield | Pump Station Seal Water System | 21CP521 | - | Wika 72039878+14298395 | - | NO | NO | 13 | 0 to 25 | Pump Station - Pressure | -edit- | 0 to 25 | +/- 1% | TH00P020GWB21CP521 | CCI-DAT-1460 | PO# 4500197977 | PRO-PID-56 | rev: 5.8 make: Wika Vendor: Wika drwg: | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | NO
144 | Tauhara B Steamfield | Pump Station Seal Water System | 22CF010 | - | SM6020, SMR12GGX50KG/US-100 | - | NO | NO |  | 0 to 10 | Pump Station - Flow | -edit- | 0 to 10 | +/- 1% | TH00P020GWB22CF010 | CCI-DAT-1474 | PO# 4500196549 | PRO-PID-56 | rev: 5.6 make: IFM Vendor: IFM drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
145 | Tauhara B Steamfield | Pump Station Seal Water System | 22CF020 | - | SM6020, SMR12GGX50KG/US-100 | - | NO | NO |  | 0 to 35 | Pump Station - Flow | -edit- | 0 to 35 | +/- 1% | TH00P020GWB22CF020 | CCI-DAT-1474 | PO# 4500196549 | PRO-PID-56 | rev: 5.6 make: IFM Vendor: IFM drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 8.75 | 17.5 | 26.25 | 35 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
146 | Tauhara B Steamfield | Pump Station Seal Water System | 22CP511 | - | Wika 72039878+14298395 | - | NO | NO | 13 | 0 to 25 | Pump Station - Pressure | -edit- | 0 to 25 | +/- 1% | TH00P020GWB22CP511 | CCI-DAT-1460 | PO# 4500197977 | PRO-PID-56 | rev: 5.8 make: Wika Vendor: Wika drwg: | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | NO
147 | Tauhara B Steamfield | Pump Station Seal Water System | 22CP521 | - | Wika 72039878+14298395 | - | NO | NO | 13 | 0 to 25 | Pump Station - Pressure | -edit- | 0 to 25 | +/- 1% | TH00P020GWB22CP521 | CCI-DAT-1460 | PO# 4500197977 | PRO-PID-56 | rev: 5.8 make: Wika Vendor: Wika drwg: | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 |  | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | NO
148 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 1120 | 0 to 1200 | Pump Station - Flow | -edit- | 0 to 1200 | +/- 1% | TH00P020LFC20CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-28 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 300 | 600 | 900 | 1200 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
149 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL001 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | NO | NO |  | 0 to 10000 | Pump Station - Level | -edit- | 0 to 10000 | +/- 1% | TH00P020LFC20CL001 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-28 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 STR-DET-0147 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2500 | 5000 | 7500 | 10000 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
150 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL002 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | NO | NO |  | 0 to 10000 | Pump Station - Level | -edit- | 0 to 10000 | +/- 1% | TH00P020LFC20CL002 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-28 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 STR-DET-0147 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2500 | 5000 | 7500 | 10000 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
151 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL003 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | NO | NO |  | 0 to 10000 | Pump Station - Level | -edit- | 0 to 10000 | +/- 1% | TH00P020LFC20CL003 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-28 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 STR-DET-0147 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2500 | 5000 | 7500 | 10000 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
152 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL010 | - | Vega B86.IXCMAXAGDHXATMKM | - | NO | NO | 0 | 0 to 6000 | Pump Station - Level | -edit- | 0 to 6000 | +/- 1% | TH00P020LFC20CL010 | CCI-DAT-1480 | PO# 4500189928 | PRO-PID-28 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: GCV-DET-0179 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1500 | 3000 | 4500 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 200 | [5 empty] | NO
153 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL020 | - | Vega B86.IXCMAXAGDHXATMKM | - | NO | NO | 0 | 0 to 6000 | Pump Station - Level | -edit- | 0 to 6000 | +/- 1% | TH00P020LFC20CL020 | CCI-DAT-1480 | PO# 4500189928 | PRO-PID-28 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: GCV-DET-0179 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1500 | 3000 | 4500 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 200 | [5 empty] | NO
154 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL030 | - | Vega B86.IXCMAXAGDHXATMKM | - | NO | NO | 0 | 0 to 6000 | Pump Station - Level | -edit- | 0 to 6000 | +/- 1% | TH00P020LFC20CL030 | CCI-DAT-1480 | PO# 4500189928 | PRO-PID-28 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: GCV-DET-0179 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1500 | 3000 | 4500 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 200 | [5 empty] | NO
155 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CL040 | - | Vega B86.IXCMAXAGDHXATMKM | - | NO | NO | 0 | 0 to 6000 | Pump Station - Level | -edit- | 0 to 6000 | +/- 1% | TH00P020LFC20CL040 | CCI-DAT-1480 | PO# 4500189928 | PRO-PID-28 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: GCV-DET-0179 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1500 | 3000 | 4500 | 6000 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 200 | [5 empty] | NO
156 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 16 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 25 | +/- 1% | TH00P020LFC20CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-28 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 3 | [5 empty] | NO
157 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT011 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 45 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020LFC20CT011 | CCI-DAT-1465 | PO# 45001918881 | PRO-PID-28 | rev: 6.3 make: Rosemount Vendor: Custom Controls drwg: STR-DET-0147 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 43 | 45 |  |  |  |  | NO
158 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT012 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT012 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
159 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT013 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT013 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
160 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT014 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT014 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
161 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT015 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT015 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
162 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT016 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT016 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
163 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT022 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT022 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
164 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT023 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT023 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
165 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT024 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT024 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
166 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT025 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT025 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
167 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CT026 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020LFC20CT026 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
168 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY010 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020LFC20CY010 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
169 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY011 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020LFC20CY011 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
170 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY012 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Speed | -edit- | - | +/- 1% | TH00P020LFC20CY012 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
171 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY020 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020LFC20CY020 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
172 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY021 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020LFC20CY021 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
173 | Tauhara B Steamfield | Pump Station Common Steam/Water Dump System | 20CY022 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Speed | -edit- | - | +/- 1% | TH00P020LFC20CY022 | PRO-DAT-0022 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
174 | Tauhara B Steamfield | Pump Station Condensate System | 10CF010 | - | Rosemount 8750WDMT2A2FNSA120CA1M4Q4Q8 | - | NO | NO | 455 | 0 to 10,000 | Pump Station - Flow | -edit- | 0 to 600 | +/- 1% | TH00P020NAB10CF010 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-28 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 150 | 300 | 450 | 600 | 0 | 4 | 8 | 12 | 16 | 20 | [6 empty] | 100 |  |  | NO
175 | Tauhara B Steamfield | Pump Station Condensate System | 10CP010 | - | Rosemount 2051CD3A02A1BS5M4Q4 | - | NO | NO | 0 | -2500 to 2500 | Pump Station - Pressure | -edit- | 0 to 250mbar | +/- 1% | TH00P020NAB10CP010 | CCI-DAT-1462 | PO# 4500191995 | PRO-PID-28 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | mbar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 200 | [5 empty] | NO
176 | Tauhara B Steamfield | Pump Station Condensate System | 10CP011 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 0.8 | -1 to 10.3 | Pump Station - Pressure | -edit- | 0 to 3 | +/- 1% | TH00P020NAB10CP011 | CCI-DAT-1461 | PO# 4500200505 | PRO-PID-28 | rev: 7.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0.75 | 1.5 | 2.25 | 3 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 0.4 |  |  |  | NO
177 | Tauhara B Steamfield | Pump Station Condensate System | 10CP012 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 3.5 | -1 to 10.3 | Pump Station - Pressure | -edit- | 0 to 10 | +/- 1% | TH00P020NAB10CP012 | CCI-DAT-1461 | PO# 4500200505 | PRO-PID-28 | rev: 7.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 9 |  | 6 |  |  |  | NO
178 | Tauhara B Steamfield | Pump Station Condensate System | 10CP030 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 3.5 | -1 to 10.3 | Pump Station - Pressure | -edit- | 0 to 10 | +/- 1% | TH00P020NAB10CP030 | CCI-DAT-1461 | PO# 4500200505 | PRO-PID-28 | rev: 7.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 9.9 | [5 empty] | NO
179 | Tauhara B Steamfield | Pump Station Condensate System | 10CT012 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NAB10CT012 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
180 | Tauhara B Steamfield | Pump Station Condensate System | 10CT013 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NAB10CT013 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
181 | Tauhara B Steamfield | Pump Station Condensate System | 10CT014 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NAB10CT014 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
182 | Tauhara B Steamfield | Pump Station Condensate System | 10CT015 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NAB10CT015 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
183 | Tauhara B Steamfield | Pump Station Condensate System | 10CT016 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NAB10CT016 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
184 | Tauhara B Steamfield | Pump Station Condensate System | 10CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 45 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020NAB10CT030 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-28 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 46 | [5 empty] | NO
185 | Tauhara B Steamfield | Pump Station Condensate System | 10CY010 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NAB10CY010 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
186 | Tauhara B Steamfield | Pump Station Condensate System | 10CY011 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NAB10CY011 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
187 | Tauhara B Steamfield | Pump Station Condensate System | 10CY012 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Speed | -edit- | - | +/- 1% | TH00P020NAB10CY012 | PRO-DAT-0021 | PO# Vendor Supplied | PRO-PID-28 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
188 | Tauhara B Steamfield | Pump Station Separated Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 1067 | 0 to 1264 tph 0 to 622.7 mb | Pump Station - Flow | -edit- | 0 to 1264 tph 0 to 622.7 mb | +/- 1% | TH00P020NDB10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-26 | rev: 7.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 316 | 632 | 948 | 1264 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
189 | Tauhara B Steamfield | Pump Station Separated Water System | 10CF020 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 1067 | 0 to 1264 tph 0 to 622.7 mb | Pump Station - Flow | -edit- | 0 to 1264 tph 0 to 622.7 mb | +/- 1% | TH00P020NDB10CF020 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-26 | rev: 7.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 316 | 632 | 948 | 1264 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 40 | 20 |  |  | NO
190 | Tauhara B Steamfield | Pump Station Separated Water System | 10CF030 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 1067 | 0 to 1264 tph 0 to 622.7 mb | Pump Station - Flow | -edit- | 0 to 1264 tph 0 to 622.7 mb | +/- 1% | TH00P020NDB10CF030 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-26 | rev: 7.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 316 | 632 | 948 | 1264 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 40 | 20 |  |  | NO
191 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP011 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP011 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 10 |  | 0.5 | 0.3 |  |  | NO
192 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP014 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP014 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
193 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP015 | - | Wika 72039917 (Model 733.14.100)++11585791 (Model 910.15) | - | NO | NO | 0 | 0 to 500 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP015 | CCI-DAT-1462 | PO# 4500189704 | PRO-PID-26 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2702 | mbar(g) | mbar | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 125 | 250 | 375 | 500 | 0 | 0 | 125 | 250 | 375 | 500 | [9 empty] | NO
194 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP021 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
195 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP024 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP024 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
196 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP025 | - | Wika 72039917 (Model 733.14.100)++11585791 (Model 910.15) | - | NO | NO | 0 | 0 to 500 | Pump Station - Pressure | -edit- | . | +/- 1% | TH00P020NDB10CP025 | CCI-DAT-1462 | PO# 4500189704 | PRO-PID-26 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2702 | mbar(g) | mbar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 125 | 250 | 375 | 500 | 0 | 0 | 125 | 250 | 375 | 500 | [9 empty] | NO
197 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP031 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP031 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 10 |  | 0.5 | 0.3 |  |  | NO
198 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP034 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP034 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
199 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP035 | - | Wika 72039917 (Model 733.14.100)++11585791 (Model 910.15) | - | NO | NO | 0 | 0 to 500 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP035 | CCI-DAT-1462 | PO# 4500189704 | PRO-PID-26 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2702 | mbar(g) | mbar | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 125 | 250 | 375 | 500 | 0 | 0 | 125 | 250 | 375 | 500 | [9 empty] | NO
200 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP040 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 35 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 45 | +/- 1% | TH00P020NDB10CP040 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 11.25 | 22.5 | 33.75 | 45 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
201 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP512 | - | Vendor Supplied Vendor Supplied | - | NO | NO | 35 | See Notes | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP512 | PRO-DAT-0020 1460 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
202 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP513 | - | Vendor Supplied Vendor Supplied | - | NO | NO | 35 | See Notes | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP513 | PRO-DAT-0020 1460 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
203 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP522 | - | Vendor Supplied Vendor Supplied | - | NO | NO | 35 | See Notes | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP522 | PRO-DAT-0020 1460 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
204 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP523 | - | Vendor Supplied Vendor Supplied | - | NO | NO | 35 | See Notes | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP523 | PRO-DAT-0020 1460 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
205 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP532 | - | Vendor Supplied Vendor Supplied | - | NO | NO | 35 | See Notes | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP532 | PRO-DAT-0020 1460 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
206 | Tauhara B Steamfield | Pump Station Separated Water System | 10CP533 | - | Vendor Supplied Vendor Supplied | - | NO | NO | 35 | See Notes | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020NDB10CP533 | PRO-DAT-0020 1460 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
207 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 123 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020NDB10CT010 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-26 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [5 empty] | 100 |  |  |  | NO
208 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT013 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT013 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
209 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT014 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT014 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
210 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT015 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT015 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
211 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT016 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT016 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
212 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT017 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT017 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
213 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT020 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 123 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020NDB10CT020 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-26 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [5 empty] | 100 |  |  |  | NO
214 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT023 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT023 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
215 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT024 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT024 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
216 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT025 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT025 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
217 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT026 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT026 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
218 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT027 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT027 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
219 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 120 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020NDB10CT030 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-26 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [5 empty] | 100 |  |  |  | NO
220 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT033 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT033 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
221 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT034 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT034 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
222 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT035 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT035 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
223 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT036 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT036 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
224 | Tauhara B Steamfield | Pump Station Separated Water System | 10CT037 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020NDB10CT037 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | NO
225 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY010 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY010 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
226 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY011 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY011 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
227 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY012 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY012 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
228 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY013 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY013 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
229 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY014 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Speed | -edit- | - | +/- 1% | TH00P020NDB10CY014 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
230 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY020 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY020 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
231 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY021 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY021 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
232 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY022 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY022 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
233 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY023 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY023 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
234 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY024 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Speed | -edit- | - | +/- 1% | TH00P020NDB10CY024 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
235 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY030 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY030 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
236 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY031 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY031 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
237 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY032 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY032 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
238 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY033 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Vibration | -edit- | - | +/- 1% | TH00P020NDB10CY033 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
239 | Tauhara B Steamfield | Pump Station Separated Water System | 10CY034 | - | Vendor Supplied Vendor Supplied | - | NO | NO | Refer to Vendor | See Notes | Pump Station - Speed | -edit- | - | +/- 1% | TH00P020NDB10CY034 | PRO-DAT-0020 | PO# Vendor Supplied | PRO-PID-26 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: Vendor Supplied | mm/s | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
240 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CF010 | - | Rosemount 8705TSA020C1W0G1B3Q4Q8+8732EMT2A2M4+ | - | NO | NO | 707 | 0 to 720 | Pump Station - Flow | -edit- | 0 to 720 | +/- 1% | TH00P020PCB20CF010 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-44 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 180 | 360 | 540 | 720 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 500 |  |  |  | NO
241 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CF020 | - | Rosemount 8705TSA020C1W0G1B3Q4Q8+8732EMT2A2M4+ | - | NO | NO | 707 | 0 to 720 | Pump Station - Flow | -edit- | 0 to 720 | +/- 1% | TH00P020PCB20CF020 | CCI-DAT-1474 | PO# 4500191995 | PRO-PID-44 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 180 | 360 | 540 | 720 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 500 |  |  |  | NO
242 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP010 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 0.9 | -1 to 10.3 | Pump Station - Pressure | -edit- | 0 to 6 | +/- 1% | TH00P020PCB20CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-44 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.5 | 3 | 4.5 | 6 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
243 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP040 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 5.82 | -1 to 10.3 | Pump Station - Pressure | -edit- | 0 to 6 | +/- 1% | TH00P020PCB20CP040 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-44 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.5 | 3 | 4.5 | 6 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 5 |  | 3 | 0.5 |  |  | NO
244 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP510 | - | Wika 72039938 (Model 433.50.100)+14503369 (IV10)+ | - | NO | NO | 0.9 | 0 to 10 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020PCB20CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-44 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | [9 empty] | NO
245 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP520 | - | Wika 72039938 (Model 433.50.100)+14503369 (IV10)+ | - | NO | NO | 5.82 | 0 to 10 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020PCB20CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-44 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | [9 empty] | NO
246 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CP530 | - | Wika 72039938 (Model 433.50.100)+14503369 (IV10)+ | - | NO | NO | 5.82 | 0 to 10 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00P020PCB20CP530 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-44 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | [9 empty] | NO
247 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 30 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB20CT010 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-46 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
248 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CT011 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 30 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB20CT011 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-46 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
249 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 20CT012 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 30 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB20CT012 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-46 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
250 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT011 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 40 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB22CT011 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-45 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 35 | [5 empty] | NO
251 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT012 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 40 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB22CT012 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-45 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 35 | [5 empty] | NO
252 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT013 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 40 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB22CT013 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-45 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 35 | [5 empty] | NO
253 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT021 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 30 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB22CT021 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-45 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 35 | [5 empty] | NO
254 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT022 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 30 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB22CT022 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-45 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 35 | [5 empty] | NO
255 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT023 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 30 | 0 to 250 | Pump Station - Temperature | -edit- | 0 to 250 | +/- 1% | TH00P020PCB22CT023 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-45 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 35 | [5 empty] | NO
256 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT031 | - | Rosemount 214CRWSMB1S4M0125SLAR1C2B1UAE065TBXW +114CM0050TAC2SC075AQ35Q5Q8XW | - | NO | NO | 30 | 0 to 250 | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020PCB22CT031 | CCI-DAT-1466 | PO# 4500197800 | PRO-PID-45 | rev: 5.9 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  | 1 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
257 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT032 | - | Rosemount 214CRWSMB1S4M0125SLAR1C2B1UAE065TBXW +114CM0050TAC2SC075AQ35Q5Q8XW | - | NO | NO | 30 | 0 to 250 | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020PCB22CT032 | CCI-DAT-1466 | PO# 4500197800 | PRO-PID-45 | rev: 5.9 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  | 2 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
258 | Tauhara B Steamfield | Pump Station VSD Cooling Water System | 22CT033 | - | Rosemount 214CRWSMB1S4M0125SLAR1C2B1UAE065TBXW +114CM0050TAC2SC075AQ35Q5Q8XW | - | NO | NO | 30 | 0 to 250 | Pump Station - Temperature | -edit- | - | +/- 1% | TH00P020PCB22CT033 | CCI-DAT-1466 | PO# 4500197800 | PRO-PID-45 | rev: 5.9 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  | 3 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
259 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 12 | +/- 1% | TH00P020QFB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-47 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3 | 6 | 9 | 12 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 10 |  |  |  | NO
260 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP020 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 12 | +/- 1% | TH00P020QFB10CP020 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-47 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3 | 6 | 9 | 12 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 10 |  |  |  | NO
261 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP030 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 12 | +/- 1% | TH00P020QFB10CP030 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-47 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3 | 6 | 9 | 12 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 10 |  |  |  | NO
262 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP040 | - | Rosemount 3051TG3A2B21BB4M4T1Q4Q8S5 | - | NO | NO | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 12 | +/- 1% | TH00P020QFB10CP040 | CCI-DAT-1461 | PO# 4500193144 | PRO-PID-47 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3 | 6 | 9 | 12 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 10 |  |  |  | NO
263 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP050 | - | Rosemount 3051TG3A2B21BB4M4T1Q4Q8S5 | - | NO | NO | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 12 | +/- 1% | TH00P020QFB10CP050 | CCI-DAT-1461 | PO# 4500193144 | PRO-PID-47 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3 | 6 | 9 | 12 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 10 |  |  |  | NO
264 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP511 | - | Wika 72039879 + 14298395 | - | NO | NO | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 16 | +/- 1% | TH00P020QFB10CP511 | CCI-DAT-1460 | PO# 4500196708 | PRO-PID-47 | rev: 6.3 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4 | 8 | 12 | 16 |  | 0 | 4 | 8 | 12 | 16 | [9 empty] | NO
265 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP521 | - | Wika 72039879 + 14298395 | - | NO | NO | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 16 | +/- 1% | TH00P020QFB10CP521 | CCI-DAT-1460 | PO# 4500196708 | PRO-PID-47 | rev: 6.3 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4 | 8 | 12 | 16 |  | 0 | 4 | 8 | 12 | 16 | [9 empty] | NO
266 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP531 | - | Wika 72039879 + 14298395 | - | NO | NO | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 16 | +/- 1% | TH00P020QFB10CP531 | CCI-DAT-1460 | PO# 4500196708 | PRO-PID-47 | rev: 6.3 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4 | 8 | 12 | 16 |  | 0 | 4 | 8 | 12 | 16 | [9 empty] | NO
267 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP541 | - | Wika 72039879 + 14298395 | - | NO | NO | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 16 | +/- 1% | TH00P020QFB10CP541 | CCI-DAT-1460 | PO# 4500196708 | PRO-PID-47 | rev: 6.3 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4 | 8 | 12 | 16 |  | 0 | 4 | 8 | 12 | 16 | [9 empty] | NO
268 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP551 | - | Wika 72039879 + 14298395 | - | NO | NO | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 16 | +/- 1% | TH00P020QFB10CP551 | CCI-DAT-1460 | PO# 4500196708 | PRO-PID-47 | rev: 6.3 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4 | 8 | 12 | 16 |  | 0 | 4 | 8 | 12 | 16 | [9 empty] | NO
269 | Tauhara B Steamfield | Pump Station Instrument Air System | 10CP523 | - | Wika 72039879 + 14298395 | - | NO | NO | 10 | -1 to 55 | Pump Station - Pressure | -edit- | 0 to 16 | +/- 1% | TH00P020QFB10CP523 | CCI-DAT-1460 | PO# 4500196708 | PRO-PID-47 | rev: 6.3 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4 | 8 | 12 | 16 |  | 0 | 4 | 8 | 12 | 16 | [9 empty] | NO
270 | Tauhara B Steamfield | Separation Plant Raw Water System | 10CL010 | - | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8 | - | NO | NO |  | See notes | Separation Plant - Level | -edit- | TBC | +/- 1% | TH00S020GAC10CL010 | CCI-DAT-1468 | PO# 4500191995 | PRO-PID-51 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: Nozzle Mount PRO-DAT-0088 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
271 | Tauhara B Steamfield | Separation Plant Raw Water System | 10CL011 | - | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8 | - | NO | NO |  | See notes | Separation Plant - Level | -edit- | TBC | +/- 1% | TH00S020GAC10CL011 | CCI-DAT-1468 | PO# 4500191995 | PRO-PID-51 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: Nozzle Mount PRO-DAT-0088 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
272 | Tauhara B Steamfield | Separation Plant Raw Water System | 10CL020 | - | Vendor Supplied Vendor Supplied | - | NO | NO |  | - | Separation Plant - Level | -edit- | Refer to Notes | +/- 1% | TH00S020GAC10CL020 | CCI-DAT-1471 PRO-DAT-0088 | PO# Vendor Supplied | PRO-PID-51 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2705 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
273 | Tauhara B Steamfield | Separation Plant Raw Water System | 10CL021 | - | Vendor Supplied Vendor Supplied | - | NO | NO |  | - | Separation Plant - Level | -edit- | Refer to Notes | +/- 1% | TH00S020GAC10CL021 | CCI-DAT-1471 PRO-DAT-0088 | PO# Vendor Supplied | PRO-PID-51 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2705 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
274 | Tauhara B Steamfield | Separation Plant Raw Water System | 10CP001 | - | Rosemount 2051CD4A02A1BS5M4Q4 | - | NO | NO | 3.49 | 0 to 20 | Separation Plant - Pressure | -edit- | 0 to 4 | +/- 1% | TH00S020GAC10CP001 | CCI-DAT-1462 | PO# 4500191995 | PRO-PID-51 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 2 | [5 empty] | NO
275 | Tauhara B Steamfield | Separation Plant Raw Water System | 10CP002 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 2.98 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020GAC10CP002 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-51 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
276 | Tauhara B Steamfield | Separation Plant Raw Water System | 21CP020 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 2.98 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 8 | +/- 1% | TH00S020GAC21CP020 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-51 | rev: 6.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2 | 4 | 6 | 8 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 4 |  | 1 |  |  |  | NO
277 | Tauhara B Steamfield | Separation Plant Raw Water System | 22CF501 | - | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - | NO | NO | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | - | +/- 1% | TH00S020GAC22CF501 | QCM-PRO-SPC-0109 | PO# 4500193000 | PRO-PID-101 | rev: 3.5 make: Brooks Vendor: Wika drwg: Vendor Designed | l/m | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
278 | Tauhara B Steamfield | Separation Plant Raw Water System | 22CF510 | - | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - | NO | NO | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | - | +/- 1% | TH00S020GAC22CF510 | QCM-PRO-SPC-0109 | PO# 4500193000 | PRO-PID-101 | rev: 3.5 make: Brooks Vendor: Wika drwg: Vendor Designed | l/m | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
279 | Tauhara B Steamfield | Separation Plant Raw Water System | 22CF520 | - | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - | NO | NO | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | - | +/- 1% | TH00S020GAC22CF520 | QCM-PRO-SPC-0109 | PO# 4500193000 | PRO-PID-100 | rev: 3.5 make: Brooks Vendor: Wika drwg: Vendor Designed | l/m | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
280 | Tauhara B Steamfield | Separation Plant Raw Water System | 22CF530 | - | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - | NO | NO | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | - | +/- 1% | TH00S020GAC22CF530 | QCM-PRO-SPC-0109 | PO# 4500193000 | PRO-PID-100 | rev: 3.5 make: Brooks Vendor: Wika drwg: Vendor Designed | l/m | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
281 | Tauhara B Steamfield | Separation Plant Raw Water System | 22CF540 | - | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - | NO | NO | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | - | +/- 1% | TH00S020GAC22CF540 | QCM-PRO-SPC-0109 | PO# 4500193000 | PRO-PID-100 | rev: 3.5 make: Brooks Vendor: Wika drwg: Vendor Designed | l/m | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
282 | Tauhara B Steamfield | Separation Plant Raw Water System | 22CF550 | - | Brooks 72040298 WR1330, BRO-2540A5L59SS-NL | - | NO | NO | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | - | +/- 1% | TH00S020GAC22CF550 | QCM-PRO-SPC-0109 | PO# 4500193000 | PRO-PID-100 | rev: 3.5 make: Brooks Vendor: Wika drwg: Vendor Designed | l/m | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
283 | Tauhara B Steamfield | Separation Plant Calcite Inhibitor Tank | 10CL010 | - | Vega PS21.XXXXXGMHB+GFL-PLUS.GG | - | NO | NO |  | 0 to 2500 | Separation Plant - Level | -edit- | 0 to 2500 | +/- 1% | TH00S020GBK10CL010 | CCI-DAT-1468 | PO# 4500193055 4500195517 | PRO-PID-53 | rev: 4.7 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 625 | 1250 | 1875 | 2500 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
284 | Tauhara B Steamfield | Separation Plant Calcite Inhibitor Sump | 10CL011 | - | Vega PS21.XXXXXGMHB+MBA.BB | - | NO | NO |  | 0 to 1000 | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020GBK10CL011 | CCI-DAT-1468 | PO# 4500193055 | PRO-PID-53 | rev: 7.7 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 250 | 500 | 750 | 1000 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
285 | Tauhara B Steamfield | Separation Plant Calcite Inhibitor Tank | 10CL020 | - | Vendor Supplied Vendor Supplied | - | NO | NO |  | 0 to 2500 | Separation Plant - Level | -edit- | 0 to 2500 | +/- 1% | TH00S020GBK10CL020 | CCI-DAT-1471 | PO# Vendor Supplied | PRO-PID-53 | rev: 2.2 make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2706 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 625 | 1250 | 1875 | 2500 | 0 | 0 | 625 | 1250 | 1875 | 2500 | [9 empty] | NO
286 | Tauhara B Steamfield | Separation Plant Potable Water System | 10CL010 | - | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8 | - | NO | NO |  | See notes | Separation Plant - Level | -edit- | TBC | +/- 1% | TH00S020GKA10CL010 | CCI-DAT-1468 | PO# 4500191995 | PRO-PID-40 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: Nozzle Mount PRO-DAT-0074 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
287 | Tauhara B Steamfield | Separation Plant Potable Water System | 10CL011 | - | Rosemount 5408F1SHA2NA1R2AACAA2M5DA1Q4Q8 | - | NO | NO |  | See notes | Separation Plant - Level | -edit- | TBC | +/- 1% | TH00S020GKA10CL011 | CCI-DAT-1468 | PO# 4500191995 | PRO-PID-40 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: Nozzle Mount PRO-DAT-0074 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
288 | Tauhara B Steamfield | Separation Plant Potable Water System | 10CL020 | - | Vendor Supplied Vendor Supplied | - | NO | NO |  | - | Separation Plant - Level | -edit- | Refer to Notes | +/- 1% | TH00S020GKA10CL020 | CCI-DAT-1471 PRO-DAT-0074 | PO# Vendor Supplied | PRO-PID-40 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2705 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
289 | Tauhara B Steamfield | Separation Plant Potable Water System | 10CL021 | - | Vendor Supplied Vendor Supplied | - | NO | NO |  | - | Separation Plant - Level | -edit- | Refer to Notes | +/- 1% | TH00S020GKA10CL021 | CCI-DAT-1471 PRO-DAT-0074 | PO# Vendor Supplied | PRO-PID-40 | rev: make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2705 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
290 | Tauhara B Steamfield | Separation Plant Potable Water System | 21CF191 | - | Wika 72039911++ (FSD-4 Model) | - | NO | NO | >1.5 | 0 to 2 | Separation Plant - Flow | -edit- |  | +/- 1% | TH00S020GKA21CF191 | CCI-DAT-1476 | PO# 4500189704 | PRO-PID-40 | rev: 6.1 make: Wika Vendor: Wika drwg: CCI-DET-2709 | kg/s | kg/s | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0.5 | 1 | 1.5 | 2 | 0 | 0 | 0.5 | 1 | 1.5 | 2 | [9 empty] | NO
291 | Tauhara B Steamfield | Separation Plant Potable Water System | 21CF192 | - | Wika 72039911++ (FSD-4 Model) | - | NO | NO | >1.5 | 0 to 2 | Separation Plant - Flow | -edit- |  | +/- 1% | TH00S020GKA21CF192 | CCI-DAT-1476 | PO# 4500189704 | PRO-PID-40 | rev: 6.1 make: Wika Vendor: Wika drwg: CCI-DET-2709 | kg/s | kg/s | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0.5 | 1 | 1.5 | 2 | 0 | 0 | 0.5 | 1 | 1.5 | 2 | [9 empty] | NO
292 | Tauhara B Steamfield | Separation Plant Potable Water System | 21CF193 | - | Wika 72039911++ (FSD-4 Model) | - | NO | NO | >1.5 | 0 to 2 | Separation Plant - Flow | -edit- |  | +/- 1% | TH00S020GKA21CF193 | CCI-DAT-1476 | PO# 4500189704 | PRO-PID-40 | rev: 6.1 make: Wika Vendor: Wika drwg: CCI-DET-2709 | kg/s | kg/s | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0.5 | 1 | 1.5 | 2 | 0 | 0 | 0.5 | 1 | 1.5 | 2 | [9 empty] | NO
293 | Tauhara B Steamfield | Separation Plant Potable Water System | 21CF194 | - | Wika 72039911++ (FSD-4 Model) | - | NO | NO | >1.5 | 0 to 4 | Separation Plant - Flow | -edit- |  | +/- 1% | TH00S020GKA21CF194 | CCI-DAT-1476 | PO# 4500189704 | PRO-PID-40 | rev: 6.1 make: Wika Vendor: Wika drwg: CCI-DET-2709 | kg/s | kg/s | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 0 | 0 | 1 | 2 | 3 | 4 | [9 empty] | NO
294 | Tauhara B Steamfield | Pump Station Potable Water System | 21CF195 | - | Wika 72039911++ (FSD-4 Model) | - | NO | NO | >1.5 | 0 to 3 | Pump Station - Flow | -edit- |  | +/- 1% | TH00S020GKA21CF195 | CCI-DAT-1476 | PO# 4500189704 | PRO-PID-40 | rev: 6.1 make: Wika Vendor: Wika drwg: CCI-DET-2709 | kg/s | kg/s | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0.75 | 1.5 | 2.25 | 3 |  | 0 | 0.75 | 1.5 | 2.25 | 3 | [9 empty] | NO
295 | Tauhara B Steamfield | Pump Station Potable Water System | 21CF196 | - | Wika 72039911++ (FSD-4 Model) | - | NO | NO | >1.5 | 0 to 3 | Pump Station - Flow | -edit- |  | +/- 1% | TH00S020GKA21CF196 | CCI-DAT-1476 | PO# 4500200070 | PRO-PID-40 | rev: 7.3 make: Wika Vendor: Wika drwg: CCI-DET-2709 | kg/s | kg/s | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0.75 | 1.5 | 2.25 | 3 |  | 0 | 0.75 | 1.5 | 2.25 | 3 | [9 empty] | NO
296 | Tauhara B Steamfield | Separation Plant Potable Water System | 20CP520 | - | Wika 72039882 (Model 433.50)+14503369+ (Model IV10) | - | NO | NO | 3.14 | 0 to 25 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020GKA20CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-40 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | NO
297 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 11CF010 | - | Vendor Supplied | - | NO | NO | - | - | Separation Plant - Flow | -edit- | 0 | +/- 1% | TH00S020GWA11CF010 |  | PO# Vendor Supplied | PRO-PID-55 | rev: 4.9 make: Vendor Supplied Vendor: Vendor Supplied drwg: | 0 | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
298 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 11CF020 | - | Vendor Supplied | - | NO | NO | - | - | Separation Plant - Flow | -edit- | 0 | +/- 1% | TH00S020GWA11CF020 |  | PO# Vendor Supplied | PRO-PID-55 | rev: 4.9 make: Vendor Supplied Vendor: Vendor Supplied drwg: | 0 | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
299 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CL310 | - | Vega P21.XXXXXABMIB | - | NO | NO | - | - | Separation Plant - Level | -edit- | 0 | +/- 1% | TH00S020GWA10CL310 |  | PO# 4500196706 | PRO-PID-55 | rev: 4.9 make: Vega Vendor: Instrumatics drwg: | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | NO
300 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 12CT010 | - | Rosemount 644HANAJ5M5Q4+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAA2SC075AQ35Q5Q8XW | - | NO | NO | 123 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020GWA12CT010 | CCI-DAT-1465 | PO# Vendor Supplied | PRO-PID-55 | rev: 4.9 make: Vendor Supplied Vendor: Vendor Supplied drwg: | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
301 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CT010 | - | Rosemount 644HANAJ5M5Q4 | - | NO | NO | 123 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020GWA10CT010 | CCI-DAT-1465 | PO# 4500200505 | PRO-PID-55 | rev: 7.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
302 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CT020 | - | Rosemount 644HANAJ5M5Q4+214CRWSMB1D3M0125SLAR1C2B1UAE065TBXW+114CM0050TAA2SC075AQ35Q5Q8XW | - | NO | NO | 123 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020GWA10CT020 | CCI-DAT-1465 | PO# 4500200505 | PRO-PID-55 | rev: 7.4 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
303 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CT010Temp | - | Servotech QT21GS2+QR08N+HKNPB | - | NO | NO | 123 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020GWA10CT010Temp | CCI-DAT-1465 | PO# 4500200319 | PRO-PID-55 | rev: 6.5 make: Servotech Vendor: Servotech drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
304 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CT020Temp | - | Servotech QT21GS2+QR08N+HKNPB | - | NO | NO | 123 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020GWA10CT020Temp | CCI-DAT-1465 | PO# 4500200319 | PRO-PID-55 | rev: 6.5 make: Servotech Vendor: Servotech drwg: CCI-DET-2703 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
305 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 11CP510 | - | Vendor Supplied Vendor Supplied | - | NO | NO | - | See notes | Separation Plant - Pressure | -edit- | 0 | +/- 1% | TH00S020GWA11CP510 |  | PO# Vendor Supplied | PRO-PID-55 | rev: 4.9 make: Vendor Supplied Vendor: Vendor Supplied drwg: | - | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | NO
306 | Tauhara B Steamfield | Separation Plant Process Water System | 10CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 7.6 | 0 to 18 | Separation Plant - Flow | -edit- | 0 to 18 | +/- 1% | TH00S020LCE10CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-18 | rev: 6.3 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4.5 | 9 | 13.5 | 18 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 5.7 |  |  |  | NO
307 | Tauhara B Steamfield | Separation Plant Process Water System | 10CF020 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 2.2 | 0 to 7.2 | Separation Plant - Flow | -edit- | 0 to 7.2 | +/- 1% | TH00S020LCE10CF020 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-20 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.8 | 3.6 | 5.4 | 7.2 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 |  | 20 | L/min |  |  | NO
308 | Tauhara B Steamfield | Separation Plant Process Water System | 10CF030 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 1.8 | 0 to 7.2 | Separation Plant - Flow | -edit- | 0 to 7.2 | +/- 1% | TH00S020LCE10CF030 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-22 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.8 | 3.6 | 5.4 | 7.2 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 |  | 20 | L/min |  |  | NO
309 | Tauhara B Steamfield | Separation Plant Process Water System | 10CF040 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 1.8 | 0 to 7.2 | Separation Plant - Flow | -edit- | 0 to 7.2 | +/- 1% | TH00S020LCE10CF040 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-24 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.8 | 3.6 | 5.4 | 7.2 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 |  | 20 | L/min |  |  | NO
310 | Tauhara B Steamfield | Separation Plant Process Water System | 10CP510 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 16.72 | 0 to 60 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020LCE10CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-18 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
311 | Tauhara B Steamfield | Separation Plant Process Water System | 10CP520 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 8.78 | 0 to 60 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020LCE10CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-20 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
312 | Tauhara B Steamfield | Separation Plant Process Water System | 10CP530 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 1.16 | 0 to 60 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020LCE10CP530 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-22 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
313 | Tauhara B Steamfield | Separation Plant Process Water System | 10CP540 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 1.16 | 0 to 60 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020LCE10CP540 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-24 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 | 0 | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
314 | Tauhara B Steamfield | Separation Plant Deoxygenated Tank 1 | 20CL010 | - | Vega PS21.XXXXXGMHB+GFL-PLUS.GG | - | NO | NO |  | 0 to 3125 | Separation Plant - Level | -edit- | 0 to 3125 | +/- 1% | TH00S020LCE20CL010 | CCI-DAT-1468 | PO# 4500193055 | PRO-PID-53 | rev: 5.6 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 781.25 | 1562.5 | 2343.75 | 3125 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
315 | Tauhara B Steamfield | Separation Plant Deoxygenated Tank 2 | 20CL011 | - | Vega PS21.XXXXXGMHB+GFL-PLUS.GG | - | NO | NO |  | 0 to 3125 | Separation Plant - Level | -edit- | 0 to 3125 | +/- 1% | TH00S020LCE20CL011 | CCI-DAT-1468 | PO# 4500193055 | PRO-PID-53 | rev: 5.6 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 781.25 | 1562.5 | 2343.75 | 3125 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
316 | Tauhara B Steamfield | Separation Plant Deoxygenated Tank 1 | 20CL020 | - | Vendor Supplied Vendor Supplied | - | NO | NO |  | 0 to 3125 | Separation Plant - Level | -edit- | 0 to 3125 | +/- 1% | TH00S020LCE20CL020 | CCI-DAT-1471 | PO# Vendor Supplied | PRO-PID-53 | rev: 2.2 make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2706 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 781.25 | 1562.5 | 2343.75 | 3125 | 0 | 0 | 781.25 | 1562.5 | 2343.75 | 3125 | [9 empty] | NO
317 | Tauhara B Steamfield | Separation Plant Deoxygenated Tank 2 | 20CL021 | - | Vendor Supplied Vendor Supplied | - | NO | NO |  | 0 to 3125 | Separation Plant - Level | -edit- | 0 to 3125 | +/- 1% | TH00S020LCE20CL021 | CCI-DAT-1471 | PO# Vendor Supplied | PRO-PID-53 | rev: 2.2 make: Vendor Supplied Vendor: Vendor Supplied drwg: CCI-DET-2706 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 781.25 | 1562.5 | 2343.75 | 3125 | 0 | 0 | 781.25 | 1562.5 | 2343.75 | 3125 | [9 empty] | NO
318 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT001 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L050NDA10CT001 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
319 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT002 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L050NDA10CT002 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
320 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT003 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L050NDA10CT003 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
321 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT011 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L060NDA10CT011 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
322 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT012 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L060NDA10CT012 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
323 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT013 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L060NDA10CT013 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
324 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT021 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L070NDA10CT021 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
325 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT022 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L070NDA10CT022 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
326 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT023 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 226.1 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00L070NDA10CT023 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-11 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
327 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT041 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 215 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA10CT041 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-18 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
328 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT042 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 215 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA10CT042 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-18 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
329 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT043 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 215 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA10CT043 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-18 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
330 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT044 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 215 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA10CT044 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-18 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
331 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT045 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 215 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA10CT045 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-18 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
332 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT046 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 215 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA10CT046 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-18 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
333 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT051 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 188 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA20CT051 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-20 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
334 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT052 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 188 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA20CT052 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-20 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
335 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT053 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 188 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA20CT053 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-20 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
336 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT054 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 188 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA20CT054 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-20 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
337 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT061 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA31CT061 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-22 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
338 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT062 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA31CT062 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-22 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
339 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT063 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA31CT063 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-22 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
340 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT064 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA31CT064 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-22 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
341 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT065 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA31CT065 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-22 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
342 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT066 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA31CT066 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-22 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
343 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT071 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA32CT071 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-24 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
344 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT072 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA32CT072 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-24 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
345 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT073 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA32CT073 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-24 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
346 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT074 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA32CT074 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-24 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
347 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT075 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA32CT075 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-24 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
348 | Tauhara B Steamfield | Separation Plant Common Steam/Water Dump System | 10CT076 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 143 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NAA32CT076 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-24 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 100 | [5 empty] | NO
349 | Tauhara B Steamfield | Separation Plant Steam System | 10CF010 | - | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0 | - | NO | NO | 740 | 0 to 900 | Separation Plant - Flow | -edit- | 0 to 900 | +/- 1% | TH00S020NAA10CF010 | CCI-DAT-1478 | PO# 4500191995 | PRO-PID-18 | rev: 5.6 make: InnovaMass Vendor: Custom Controls drwg: MEC-DET-1045 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 225 | 450 | 675 | 900 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
350 | Tauhara B Steamfield | Separation Plant Steam System | 10CL410 | - | Bliss Anand R/36/M/S/2/1/B/N/N/X/PN/S/772MM | - | NO | NO | - | - | Separation Plant - Level | -edit- | 0 to 800 | +/- 1% | TH00S020NAA10CL410 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-18 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type HP08 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 200 | 400 | 600 | 800 | 0 | 0 | 200 | 400 | 600 | 800 | [9 empty] | NO
351 | Tauhara B Steamfield | Separation Plant Steam System | 10CL450 | - | Bliss Anand R/47/M/S/2/1/B/N/N/X/PN/S/1156MM | - | NO | NO |  | - | Separation Plant - Level | -edit- | 0 to 1200 | +/- 1% | TH00S020NAA10CL450 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-19 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type HP12 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 300 | 600 | 900 | 1200 | 0 | 0 | 300 | 600 | 900 | 1200 | [9 empty] | NO
352 | Tauhara B Steamfield | Separation Plant Steam System | 10CL451 | - | Rosemount 5301HA2P1N4AM00120ABNAM1Q4Q8QTDA1S2 | - | NO | NO |  | 0 to 1200 | Separation Plant - Level | -edit- | 0 to 1200 | +/- 1% | TH00S020NAA10CL451 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-19 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: 000-MEC-DET-1231 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 300 | 600 | 900 | 1200 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 1100 |  | 100 |  |  |  | NO
353 | Tauhara B Steamfield | Separation Plant Steam System | 10CL460 | - | Bliss Anand R/36/M/S/2/1/B/N/N/X/PN/S/772MM | - | NO | NO |  | - | Separation Plant - Level | -edit- | 0 to 800 | +/- 1% | TH00S020NAA10CL460 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-19 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type HP08 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 200 | 400 | 600 | 800 | 0 | 0 | 200 | 400 | 600 | 800 | [9 empty] | NO
354 | Tauhara B Steamfield | Separation Plant Steam System | 10CP021 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NAA10CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
355 | Tauhara B Steamfield | Separation Plant Steam System | 10CP022 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NAA10CP022 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
356 | Tauhara B Steamfield | Separation Plant Steam System | 10CP023 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NAA10CP023 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
357 | Tauhara B Steamfield | Separation Plant Steam System | 10CP031 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - | NO | NO | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NAA10CP031 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
358 | Tauhara B Steamfield | Separation Plant Steam System | 10CP032 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - | NO | NO | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NAA10CP032 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
359 | Tauhara B Steamfield | Separation Plant Steam System | 10CP033 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - | NO | NO | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NAA10CP033 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
360 | Tauhara B Steamfield | Separation Plant Steam System | 11CF452 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 8.7 | 0 to 20 | Separation Plant - Flow | -edit- | 0 to 18 | +/- 1% | TH00S020NAA11CF452 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-19 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4.5 | 9 | 13.5 | 18 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 250 |  | 20 |  |  |  | NO
361 | Tauhara B Steamfield | Separation Plant Steam System | 20CF010 | - | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0 | - | NO | NO | 191 | 0 to 216 | Separation Plant - Flow | -edit- | 0 to 216 | +/- 1% | TH00S020NAA20CF010 | CCI-DAT-1478 | PO# 4500191995 | PRO-PID-21 | rev: 5.6 make: InnovaMass Vendor: Custom Controls drwg: MEC-DET-1045 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 54 | 108 | 162 | 216 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
362 | Tauhara B Steamfield | Separation Plant Steam System | 20CL410 | - | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM | - | NO | NO |  | - | Separation Plant - Level | -edit- | 0 to 600 | +/- 1% | TH00S020NAA20CL410 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-20 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type IP06 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 150 | 300 | 450 | 600 | 0 | 0 | 150 | 300 | 450 | 600 | [9 empty] | NO
363 | Tauhara B Steamfield | Separation Plant Steam System | 20CL450 | - | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM | - | NO | NO |  | - | Separation Plant - Level | -edit- | 0 to 600 | +/- 1% | TH00S020NAA20CL450 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-21 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type IP06 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 150 | 300 | 450 | 600 | 0 | 0 | 150 | 300 | 450 | 600 | [9 empty] | NO
364 | Tauhara B Steamfield | Separation Plant Steam System | 20CL460 | - | Bliss Anand R/27/M/S/2/1/B/N/N/X/PN/S/559MM | - | NO | NO |  | - | Separation Plant - Level | -edit- | 0 to 600 | +/- 1% | TH00S020NAA20CL460 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-21 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type IP06 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 150 | 300 | 450 | 600 | 0 | 0 | 150 | 300 | 450 | 600 | [9 empty] | NO
365 | Tauhara B Steamfield | Separation Plant Steam System | 20CP021 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 15 | +/- 1% | TH00S020NAA20CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-20 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
366 | Tauhara B Steamfield | Separation Plant Steam System | 20CP022 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 15 | +/- 1% | TH00S020NAA20CP022 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-20 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
367 | Tauhara B Steamfield | Separation Plant Steam System | 20CP023 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 15 | +/- 1% | TH00S020NAA20CP023 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-20 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
368 | Tauhara B Steamfield | Separation Plant Steam System | 20CP031 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - | NO | NO | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 13 | +/- 1% | TH00S020NAA20CP031 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-20 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.25 | 6.5 | 9.75 | 13 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
369 | Tauhara B Steamfield | Separation Plant Steam System | 20CP032 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - | NO | NO | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 13 | +/- 1% | TH00S020NAA20CP032 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-20 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.25 | 6.5 | 9.75 | 13 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
370 | Tauhara B Steamfield | Separation Plant Steam System | 20CP033 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8QT | - | NO | NO | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 13 | +/- 1% | TH00S020NAA20CP033 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-20 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.25 | 6.5 | 9.75 | 13 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
371 | Tauhara B Steamfield | Separation Plant Steam System | 31CF010 | - | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0 | - | NO | NO | 162 | 0 to 216 | Separation Plant - Flow | -edit- | 0 to 216 | +/- 1% | TH00S020NAA31CF010 | CCI-DAT-1478 | PO# 4500191995 | PRO-PID-22 | rev: 5.6 make: InnovaMass Vendor: Custom Controls drwg: MEC-DET-1045 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 54 | 108 | 162 | 216 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
372 | Tauhara B Steamfield | Separation Plant Steam System | 31CL410 | - | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - | NO | NO |  | - | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020NAA31CL410 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-22 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type LP10 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 250 | 500 | 750 | 1000 | 0 | 0 | 250 | 500 | 750 | 1000 | [9 empty] | NO
373 | Tauhara B Steamfield | Separation Plant Steam System | 31CL450 | - | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - | NO | NO |  | - | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020NAA31CL450 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-23 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type LP10 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 250 | 500 | 750 | 1000 | 0 | 0 | 250 | 500 | 750 | 1000 | [9 empty] | NO
374 | Tauhara B Steamfield | Separation Plant Steam System | 31CL460 | - | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - | NO | NO |  | - | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020NAA31CL460 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-23 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type LP10 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 250 | 500 | 750 | 1000 | 0 | 0 | 250 | 500 | 750 | 1000 | [9 empty] | NO
375 | Tauhara B Steamfield | Separation Plant Steam System | 31CP021 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA31CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
376 | Tauhara B Steamfield | Separation Plant Steam System | 31CP022 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA31CP022 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
377 | Tauhara B Steamfield | Separation Plant Steam System | 31CP023 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA31CP023 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
378 | Tauhara B Steamfield | Separation Plant Steam System | 31CP031 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA31CP031 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
379 | Tauhara B Steamfield | Separation Plant Steam System | 31CP032 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA31CP032 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
380 | Tauhara B Steamfield | Separation Plant Steam System | 31CP033 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA31CP033 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
381 | Tauhara B Steamfield | Separation Plant Steam System | 32CF010 | - | InnovaMass 241S‐VT‐LS‐E2‐DD‐PV1L‐V4LH‐ST‐MP0 | - | NO | NO | 162 | 0 to 216 | Separation Plant - Flow | -edit- | 0 to 216 | +/- 1% | TH00S020NAA32CF010 | CCI-DAT-1478 | PO# 4500191995 | PRO-PID-24 | rev: 5.6 make: InnovaMass Vendor: Custom Controls drwg: MEC-DET-1045 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 54 | 108 | 162 | 216 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
382 | Tauhara B Steamfield | Separation Plant Steam System | 32CL410 | - | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - | NO | NO |  | - | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020NAA32CL410 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-24 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type LP10 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 250 | 500 | 750 | 1000 | 0 | 0 | 250 | 500 | 750 | 1000 | [9 empty] | NO
383 | Tauhara B Steamfield | Separation Plant Steam System | 32CL450 | - | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - | NO | NO |  | - | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020NAA32CL450 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-25 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type LP10 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 250 | 500 | 750 | 1000 | 0 | 0 | 250 | 500 | 750 | 1000 | [9 empty] | NO
384 | Tauhara B Steamfield | Separation Plant Steam System | 32CL460 | - | Bliss Anand R/38/M/S/2/1/B/N/N/X/PN/S/981MM | - | NO | NO |  | - | Separation Plant - Level | -edit- | 0 to 1000 | +/- 1% | TH00S020NAA32CL460 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-25 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: MEC-DET-1230 LG Type LP10 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 250 | 500 | 750 | 1000 | 0 | 0 | 250 | 500 | 750 | 1000 | [9 empty] | NO
385 | Tauhara B Steamfield | Separation Plant Steam System | 32CP021 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA32CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
386 | Tauhara B Steamfield | Separation Plant Steam System | 32CP022 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA32CP022 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
387 | Tauhara B Steamfield | Separation Plant Steam System | 32CP023 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA32CP023 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
388 | Tauhara B Steamfield | Separation Plant Steam System | 32CP031 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA32CP031 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
389 | Tauhara B Steamfield | Separation Plant Steam System | 32CP032 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA32CP032 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
390 | Tauhara B Steamfield | Separation Plant Steam System | 32CP033 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8QT | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NAA32CP033 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
391 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL011 | - | Rosemount 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA10CL011 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-12 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1052 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
392 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL012 | - | Rosemount 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA10CL012 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-12 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1052 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
393 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL013 | - | Rosemount 5301HA2P1N4AM00268BBNAM1Q4Q8QTDA1S3 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA10CL013 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-12 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1052 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
394 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL014 | - | Rosemount 3051S2CD3A2B12A1BM5Q4Q8Q15 | - | NO | NO | - | 0 to 5690 | Separation Plant - Level | -edit- | 0 to 5690 | +/- 1% | TH00S020NDA10CL014 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-12 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 MEC-SCN-3036 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1422.5 | 2845 | 4267.5 | 5690 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
395 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL021 | - | Rosemount 3051S2CD2A2B12A1BM5Q4Q8Q15 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA10CL021 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-12 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1050 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
396 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL022 | - | Rosemount 3051S2CD2A2B12A1BM5Q4Q8Q15 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA10CL022 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-12 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1050 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
397 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL023 | - | Rosemount 3051S2CD2A2B12A1BM5Q4Q8Q15 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA10CL023 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-12 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1050 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
398 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CL031 | - | Bliss Anand R/88/M/S/2/1/B/N/N/X/PN/S/2560MM | - | NO | NO | 1676 | - | Separation Plant - Level | -edit- | 335 to 3018 | +/- 1% | TH00S020NDA10CL031 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-12 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: CCI-DET-2705 NDA-MEC-DET-1050 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 670 | 1340 | 2010 | 2680 | 0 | 0 | 670 | 1340 | 2010 | 2680 | [9 empty] | NO
399 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 23 | +/- 1% | TH00S020NDA10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-12 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 5.75 | 11.5 | 17.25 | 23 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
400 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 217.9 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NDA10CT010 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-11 | rev: 4.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
401 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CT020 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 217.9 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NDA10CT020 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-11 | rev: 4.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
402 | Tauhara B Steamfield | Separation Plant Production Piping System | 10CT030 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 217.9 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NDA10CT030 | CCI-DAT-1465 | PO# 4500191995 | PRO-PID-11 | rev: 4.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
403 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 2530 | 0 to 3222 | Separation Plant - Flow | -edit- | 0 to 3222 | +/- 1% | TH00S020NDA20CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-12 | rev: 6.3 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 805.5 | 1611 | 2416.5 | 3222 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
404 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CF020 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 2916 | 0 to 3222 | Separation Plant - Flow | -edit- | 0 to 3222 | +/- 1% | TH00S020NDA20CF020 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-12 | rev: 6.3 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | tph | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 805.5 | 1611 | 2416.5 | 3222 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
405 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL011 | - | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA20CL011 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-13 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1055 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
406 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL012 | - | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA20CL012 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-13 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1055 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
407 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL013 | - | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA20CL013 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-13 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1055 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
408 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL014 | - | Rosemount 3051S2CD3A2B12A1BM5Q4Q8Q15 | - | NO | NO | - | 0 to 5440 | Separation Plant - Level | -edit- | 0 to 5440 | +/- 1% | TH00S020NDA20CL014 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-13 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 MEC-SCN-3038 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1360 | 2720 | 4080 | 5440 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
409 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL021 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA20CL021 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-13 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1053 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
410 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL022 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA20CL022 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-13 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1053 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
411 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL023 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA20CL023 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-13 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1053 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
412 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CL031 | - | Bliss Anand R/88/M/S/2/1/B/N/N/X/PN/S/2560MM | - | NO | NO | 1676 | - | Separation Plant - Level | -edit- | 335 to 3018 | +/- 1% | TH00S020NDA20CL031 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-13 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: CCI-DET-2705 NDA-MEC-DET-1053 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 670 | 1340 | 2010 | 2680 | 0 | 0 | 670 | 1340 | 2010 | 2680 | [9 empty] | NO
413 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 9 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 15 | +/- 1% | TH00S020NDA20CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-13 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 3.75 | 7.5 | 11.25 | 15 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
414 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CR001 | - | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - | NO | NO | * | TBC | Separation Plant - Corrosometer | -edit- | TBC | +/- 1% | TH00S020NDA20CR001 | COSASCO Model 3500/3500HT ER-420 | PO# 4500189863 | PRO-PID-12 | rev: 5.6 make: Cosasco Vendor: Cosasco drwg: TBC | mm/Time Unit | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
415 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CR002 | - | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - | NO | NO | * | TBC | Separation Plant - Corrosometer | -edit- | TBC | +/- 1% | TH00S020NDA20CR002 | COSASCO Model 3500/3500HT ER-420 | PO# 4500189863 | PRO-PID-12 | rev: 5.6 make: Cosasco Vendor: Cosasco drwg: TBC | mm/Time Unit | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
416 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CR003 | - | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - | NO | NO | * | TBC | Separation Plant - Corrosometer | -edit- | TBC | +/- 1% | TH00S020NDA20CR003 | COSASCO Model 3500/3500HT ER-420 | PO# 4500189863 | PRO-PID-12 | rev: 5.6 make: Cosasco Vendor: Cosasco drwg: TBC | mm/Time Unit | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
417 | Tauhara B Steamfield | Separation Plant Production Piping System | 20CR004 | - | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - | NO | NO | * | TBC | Separation Plant - Corrosometer | -edit- | TBC | +/- 1% | TH00S020NDA30CR004 | COSASCO Model 3500/3500HT ER-420 | PO# 4500189863 | PRO-PID-13 | rev: 6.5 make: Cosasco Vendor: Cosasco drwg: 1" NPT | mm/Time Unit | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
418 | Tauhara B Steamfield | Separation Plant Production Piping System | 21CF010 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 450 | 0 to 495 | Separation Plant - Flow | -edit- | 0 to 495 | +/- 1% | TH00S020NDA21CF010 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-30 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 123.75 | 247.5 | 371.25 | 495 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 15 | L/min |  |  | NO
419 | Tauhara B Steamfield | Separation Plant Production Piping System | 21CP010 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 25 | +/- 1% | TH00S020NDA21CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-30 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
420 | Tauhara B Steamfield | Separation Plant Production Piping System | 21CP011 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 18.8 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 25 | +/- 1% | TH00S020NDA21CP011 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-30 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2701 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
421 | Tauhara B Steamfield | Separation Plant Production Piping System | 21CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 202 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NDA21CT010 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-30 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 200 | [5 empty] | NO
422 | Tauhara B Steamfield | Separation Plant Production Piping System | 22CF020 | - | Rosemount 3051S1CD2A2A11A1BM5P1Q4Q8T1 | - | NO | NO | 450 | 0 to 495 | Separation Plant - Flow | -edit- | 0 to 495 | +/- 1% | TH00S020NDA22CF020 | CCI-DAT-1472 PRO-CAL-0039 | PO# 4500191995 | PRO-PID-30 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2702 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 123.75 | 247.5 | 371.25 | 495 | 0 | 4 | 8 | 12 | 16 | 20 | [5 empty] | 15 | L/min |  |  | NO
423 | Tauhara B Steamfield | Separation Plant Production Piping System | 22CP020 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 17 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 25 | +/- 1% | TH00S020NDA22CP020 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-30 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
424 | Tauhara B Steamfield | Separation Plant Production Piping System | 22CP021 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 18.8 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 25 | +/- 1% | TH00S020NDA22CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-30 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2701 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
425 | Tauhara B Steamfield | Separation Plant Production Piping System | 22CT020 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 202 | 0 to 250 | Separation Plant - Temperature | -edit- | 0 to 250 | +/- 1% | TH00S020NDA22CT020 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-30 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  |  |  | 200 | [5 empty] | NO
426 | Tauhara B Steamfield | Separation Plant Production Piping System | 23CF011 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - | NO | NO | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | Refer to Specification | +/- 1% | TH00S020NDA23CF011 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-101 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8 |  | 2 |  |  |  | NO
427 | Tauhara B Steamfield | Separation Plant Production Piping System | 23CP511 | - | Rosemount 3051CD3A02A1BS5M4Q4Q8T1Q15 | - | NO | NO | 0.23 | 0 to 20 | Separation Plant - Pressure | -edit- | 0 to 20 | +/- 1% | TH00S020NDA23CP511 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-101 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 5 | 10 | 15 | 20 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 2 | [5 empty] | NO
428 | Tauhara B Steamfield | Separation Plant Production Piping System | 23CP512 | - | Wika 72039878+14503369+0731277 | - | NO | NO | 8 | 0 to 25 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020NDA23CP512 | QCM-PRO-SPC-0109 | PO# 4500198881 | PRO-PID-101 | rev: 7.5 make: Wika Vendor: Wika drwg: Vendor Designed | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | NO
429 | Tauhara B Steamfield | Separation Plant Production Piping System | 23CQ010 | - | E+H CM442-EL64/0 + CPS47E-10C2/0 + CYK10-A051 | - | NO | NO | 5 | 0 to 14 | Separation Plant - Analyser | -edit- | 3.5 to 8.5 | +/- 1% | TH00S020NDA23CQ010 | QCM-PRO-SPC-0109 | PO# 4500191501 | PRO-PID-101 | rev: make: E+H Vendor: EMC drwg: Vendor Designed | pH | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 3.5 | 4.75 | 6 | 7.25 | 8.5 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 5.5 |  | 4.5 |  |  |  | NO
430 | Tauhara B Steamfield | Separation Plant Production Piping System | 23CT011 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 60 | 0 to 215 | Separation Plant - Temperature | -edit- | 0 to 100 | +/- 1% | TH00S020NDA23CT011 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-101 | rev: 4.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | 50 |  |  |  |  | NO
431 | Tauhara B Steamfield | Separation Plant Production Piping System | 24CF020 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - | NO | NO | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | Refer to Specification | +/- 1% | TH00S020NDA24CF020 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-101 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8 |  | 2 |  |  |  | NO
432 | Tauhara B Steamfield | Separation Plant Production Piping System | 24CP521 | - | Rosemount 3051CD3A02A1BS5M4Q4Q8T1Q15 | - | NO | NO | 0.23 | 0 to 20 | Separation Plant - Pressure | -edit- | 0 to 20 | +/- 1% | TH00S020NDA24CP521 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-101 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 5 | 10 | 15 | 20 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 2 | [5 empty] | NO
433 | Tauhara B Steamfield | Separation Plant Production Piping System | 24CP522 | - | Wika 72039878+14503369+0731277 | - | NO | NO | 8 | 0 to 25 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020NDA24CP522 | QCM-PRO-SPC-0109 | PO# 4500198881 | PRO-PID-101 | rev: 7.5 make: Wika Vendor: Wika drwg: Vendor Designed | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 | [9 empty] | NO
434 | Tauhara B Steamfield | Separation Plant Production Piping System | 24CQ020 | - | E+H CM442-EL64/0 + CPS47E-10C2/0 | - | NO | NO | 5 | 0 to 14 | Separation Plant - Analyser | -edit- | 3.5 to 8.5 | +/- 1% | TH00S020NDA24CQ020 | QCM-PRO-SPC-0109 | PO# 4500191501 | PRO-PID-101 | rev: make: E+H Vendor: EMC drwg: Vendor Designed | pH | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 3.5 | 4.75 | 6 | 7.25 | 8.5 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 5.5 |  | 4.5 |  |  |  | NO
435 | Tauhara B Steamfield | Separation Plant Production Piping System | 24CT021 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 60 | 0 to 215 | Separation Plant - Temperature | -edit- | 0 to 100 | +/- 1% | TH00S020NDA24CT021 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-101 | rev: 4.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | 50 |  |  |  |  | NO
436 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL011 | - | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA30CL011 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-14 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1055 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
437 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL012 | - | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA30CL012 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-14 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1055 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
438 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL013 | - | Rosemount 5301HA2P1N4AM00268BANAM1Q4Q8QTDA1S3 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA30CL013 | CCI-DAT-1469 | PO# 4500191995 | PRO-PID-14 | rev: 3.2 make: Rosemount Vendor: Custom Controls drwg: NDA-MEC-DET-1055 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 670 | 1340 | 2010 | 2680 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
439 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL014 | - | Rosemount 3051S2CD3A2B12A1BM5Q4Q8Q15 | - | NO | NO | - | 0 to 5640 | Separation Plant - Level | -edit- | 0 to 5640 | +/- 1% | TH00S020NDA30CL014 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-14 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 MEC-SCN-3039 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1410 | 2820 | 4230 | 5640 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
440 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL015 | - | Rosemount 3051S2CD3A2B12A1BM5Q4Q8Q15 | - | NO | NO | - | 0 to 5640 | Separation Plant - Level | -edit- | 0 to 5640 | +/- 1% | TH00S020NDA30CL015 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-14 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1410 | 2820 | 4230 | 5640 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
441 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL021 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA30CL021 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-14 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1053 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
442 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL022 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA30CL022 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-14 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1053 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
443 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL023 | - | Rosemount 2051CD3A22A1BS2M4Q4Q8Q15 | - | NO | NO | 1676 | 0 to 2680 | Separation Plant - Level | -edit- | 335 to 3015 | +/- 1% | TH00S020NDA30CL023 | CCI-DAT-1467 | PO# 4500200843 | PRO-PID-14 | rev: 7.0 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2704 NDA-MEC-DET-1053 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 335 | 1005 | 1675 | 2345 | 3015 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
444 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CL031 | - | Bliss Anand R/88/M/S/2/1/B/N/N/X/PN/S/2560MM | - | NO | NO | 1676 | - | Separation Plant - Level | -edit- | 335 to 3018 | +/- 1% | TH00S020NDA30CL031 | CCI-DAT-1471 | PO# 4500193407 | PRO-PID-14 | rev: 6.0 make: Bliss Anand Vendor: Powerflo Solutions drwg: CCI-DET-2705 NDA-MEC-DET-1053 | mm | mm | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 670 | 1340 | 2010 | 2680 | 0 | 0 | 670 | 1340 | 2010 | 2680 | [9 empty] | NO
445 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CP011 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NDA30CP011 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 6.2 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
446 | Tauhara B Steamfield | Separation Plant Production Piping System | 30CP012 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 1 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 5 | +/- 1% | TH00S020NDA30CP012 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-14 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
447 | Tauhara B Steamfield | Separation Plant Separated Water System | 10CP010 | - | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 2.6 | -1 to 10.3 | Separation Plant - Pressure | -edit- | 0 to 10 | +/- 1% | TH00S020NDB10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-26 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
448 | Tauhara B Steamfield | Separation Plant Separated Water System | 11CF011 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - | NO | NO | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | 0 to 10 | +/- 1% | TH00S020NDB11CF011 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8 |  | 2 |  |  |  | NO
449 | Tauhara B Steamfield | Separation Plant Separated Water System | 11CQ010 | - | E+H CM442-EL64/0 + CPS47E-10C2/0 | - | NO | NO | 5 | 0 to 14 | Separation Plant - Analyser | -edit- | 3.5 to 8.5 | +/- 1% | TH00S020NDB11CQ010 | QCM-PRO-DAT-0108 | PO# 4500191501 | PRO-PID-100 | rev: make: E+H Vendor: EMC drwg: Vendor Designed | pH | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 3.5 | 4.75 | 6 | 7.25 | 8.5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
450 | Tauhara B Steamfield | Separation Plant Separated Water System | 11CT011 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 60 | 0 to 75 | Separation Plant - Temperature | -edit- | 0 to 100 | +/- 1% | TH00S020NDB11CT011 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 4.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | 50 |  |  |  |  | NO
451 | Tauhara B Steamfield | Separation Plant Separated Water System | 12CF021 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - | NO | NO | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | Refer to Specification | +/- 1% | TH00S020NDB12CF021 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8 |  | 2 |  |  |  | NO
452 | Tauhara B Steamfield | Separation Plant Separated Water System | 12CQ020 | - | E+H CM442-EL64/0 + CPS47E-10C2/0 | - | NO | NO | 5 | 0 to 14 | Separation Plant - Analyser | -edit- | 3.5 to 8.5 | +/- 1% | TH00S020NDB12CQ020 | QCM-PRO-SPC-0109 | PO# 4500191501 | PRO-PID-100 | rev: make: E+H Vendor: EMC drwg: Vendor Designed | pH | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 3.5 | 4.75 | 6 | 7.25 | 8.5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
453 | Tauhara B Steamfield | Separation Plant Separated Water System | 12CT021 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 60 | 0 to 75 | Separation Plant - Temperature | -edit- | 0 to 100 | +/- 1% | TH00S020NDB12CT021 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 4.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | 50 |  |  |  |  | NO
454 | Tauhara B Steamfield | Separation Plant Separated Water System | 13CF031 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - | NO | NO | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | Refer to Specification | +/- 1% | TH00S020NDB13CF031 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8 |  | 2 |  |  |  | NO
455 | Tauhara B Steamfield | Separation Plant Separated Water System | 13CQ030 | - | E+H CM442-EL64/0 | - | NO | NO | 5 | 0 to 14 | Separation Plant - Analyser | -edit- | 3.5 to 8.5 | +/- 1% | TH00S020NDB13CQ030 | QCM-PRO-SPC-0109 | PO# 4500191501 | PRO-PID-100 | rev: make: E+H Vendor: EMC drwg: Vendor Designed | pH | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 3.5 | 4.75 | 6 | 7.25 | 8.5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
456 | Tauhara B Steamfield | Separation Plant Separated Water System | 13CT031 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 60 | 0 to 75 | Separation Plant - Temperature | -edit- | 0 to 100 | +/- 1% | TH00S020NDB13CT031 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 4.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | 50 |  |  |  |  | NO
457 | Tauhara B Steamfield | Separation Plant Separated Water System | 14CF041 | - | Rosemount 8705TSA005C3W0G1B3Q4Q8+8732EMT2A2M4 | - | NO | NO | Refer to Specification | Refer to Specification | Separation Plant - Flow | -edit- | Refer to Specification | +/- 1% | TH00S020NDB14CF041 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 8 |  | 2 |  |  |  | NO
458 | Tauhara B Steamfield | Separation Plant Separated Water System | 14CQ040 | - | E+H CM442-EL64/0 | - | NO | NO | 5 | 0 to 14 | Separation Plant - Analyser | -edit- | 3.5 to 8.5 | +/- 1% | TH00S020NDB14CQ040 | QCM-PRO-SPC-0109 | PO# 4500191501 | PRO-PID-100 | rev: make: E+H Vendor: EMC drwg: Vendor Designed | pH | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 3.5 | 4.75 | 6 | 7.25 | 8.5 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
459 | Tauhara B Steamfield | Separation Plant Separated Water System | 14CT041 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 60 | 0 to 75 | Separation Plant - Temperature | -edit- | 0 to 100 | +/- 1% | TH00S020NDB14CT041 | QCM-PRO-SPC-0109 | PO# 4500192700 | PRO-PID-100 | rev: 4.6 make: Rosemount Vendor: Custom Controls drwg: Vendor Designed | °C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 30 | 50 |  |  |  |  | NO
460 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CL010 | - | Vega PS31.XXXXXGMHB +GFLK.ADGX | - | NO | NO |  | 0 to 4500 | Separation Plant - Level | -edit- | TBC | +/- 1% | TH00S020QCM10CL010 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-29 | rev: 6.5 make: Vega Vendor: Instrumatics drwg: Nozzle mount QCM-PRO-DAT-0071 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1125 | 2250 | 3375 | 4500 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 95 | 95 | 10 |  |  |  | NO
461 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10CL020 | - | Vega PS31.XXXXXGMHB +GFLK.ADGX | - | NO | NO |  | 0 to 4500 | Separation Plant - Level | -edit- | TBC | +/- 1% | TH00S020QCM10CL020 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-29 | rev: 6.5 make: Vega Vendor: Instrumatics drwg: Nozzle mount QCM-PRO-DAT-0071 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1125 | 2250 | 3375 | 4500 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 95 | 95 | 10 |  |  |  | NO
462 | Tauhara B Steamfield | !@! Separation Plant Acid Dosing System | 10CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 20 | -5 to 50 | Separation Plant - Temperature | -edit- | -5 to 50 | +/- 1% | TH00S020QCM10CT010 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-29 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 QCM-PRO-DAT-0071 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -5 | 8.75 | 22.5 | 36.25 | 50 | 0 | -5 | 8.75 | 22.5 | 36.25 | 50 | [9 empty] | NO
463 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10DL0020 | - | Vega TKALM3-HMI-DB | - | NO | NO |  | See notes | Separation Plant - Level | -edit- | 0-100% | +/- 1% | TH00S020QCM10DL0020 | CCI-DAT-1470 | PO# 4500189544 | PRO-PID-29 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2720 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
464 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 10EH011 | - | Vega See S020QCM10DL0020 | - | NO | NO |  |  | Separation Plant - Level | -edit- |  | +/- 1% | TH00S020QCM10EH011 |  | PO# 4500189544 | PRO-PID-29 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2720 | mm | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | - | - | - | - | [9 empty] | NO
465 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CF010 | - | Yokogawa AX005-GA000BA2AT224B-2JA11/GRT | - | NO | NO | 2.2 | 0-3 | Separation Plant - Flow | -edit- | 0 to 2.5 | +/- 1% | TH00S020QCM20CF010 | CCI-DAT-1474 | PO# 4500201023 | PRO-PID-30 | rev: 7.1 make: Yokogawa Vendor: Yokogawa drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0.625 | 1.25 | 1.875 | 2.5 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 2 |  | 0.5 |  |  |  | NO
466 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CP011 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 18.4 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 30 | +/- 1% | TH00S020QCM20CP011 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-30 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 7.5 | 15 | 22.5 | 30 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 27 | [5 empty] | NO
467 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CP501 | - | Wika 72039899+14503369+ | - | NO | NO | 0.3 | 0 to 5 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020QCM20CP501 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-30 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | [9 empty] | NO
468 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CP510 | - | Wika 72039915 (Model 433.56.100)+14503369 (Model IV10)+ | - | NO | NO | 18.4 | 0 to 40 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020QCM20CP510 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-30 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 10 | 20 | 30 | 40 | 0 | 0 | 10 | 20 | 30 | 40 | [9 empty] | NO
469 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 20CT010 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 20 | -5 to 50 | Separation Plant - Temperature | -edit- | -5 to 50 | +/- 1% | TH00S020QCM20CT010 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-30 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -5 | 8.75 | 22.5 | 36.25 | 50 | 0 | -5 | 8.75 | 22.5 | 36.25 | 50 | [9 empty] | NO
470 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CF020 | - | Yokogawa AX005-GA000BA2AT224B-2JA11/GRT | - | NO | NO | 2.2 | 0-3 | Separation Plant - Flow | -edit- | 0 to 2.5 | +/- 1% | TH00S020QCM21CF020 | CCI-DAT-1474 | PO# 4500201023 | PRO-PID-30 | rev: 7.1 make: Yokogawa Vendor: Yokogawa drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0.625 | 1.25 | 1.875 | 2.5 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 2 |  | 0.5 |  |  |  | NO
471 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CF010Temp | - | IFM SI5004+E40107 | - | NO | NO | 2.2 | 0-3 | Separation Plant - Flow | -edit- | 0 to 2.5 | +/- 1% | TH00S020QCM21CF010Temp | CCI-DAT-1474 | PO# 4500200797 | PRO-PID-30 | rev: 7.0 make: IFM Vendor: IFM drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0.625 | 1.25 | 1.875 | 2.5 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
472 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CF020Temp | - | IFM SI5004+E40107 | - | NO | NO | 2.2 | 0-3 | Separation Plant - Flow | -edit- | 0 to 2.5 | +/- 1% | TH00S020QCM21CF020Temp | CCI-DAT-1474 | PO# 4500200797 | PRO-PID-30 | rev: 7.0 make: IFM Vendor: IFM drwg: CCI-DET-2707 | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0.625 | 1.25 | 1.875 | 2.5 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
473 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CP021 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 18.4 | -1 to 55 | Separation Plant - Pressure | -edit- | 0 to 30 | +/- 1% | TH00S020QCM21CP021 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-30 | rev: 3.8 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 7.5 | 15 | 22.5 | 30 | 0 | 4 | 8 | 12 | 16 | 20 |  |  |  | 27 | [5 empty] | NO
474 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CP502 | - | Wika 72039899+14503369+ | - | NO | NO | 0.3 | 0 to 5 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020QCM21CP502 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-30 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | 0 | 0 | 1.25 | 2.5 | 3.75 | 5 | [9 empty] | NO
475 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CP520 | - | Wika 72039915 (Model 433.56.100)+14503369 (Model IV10)+ | - | NO | NO | 18.4 | 0 to 40 | Separation Plant - Pressure | -edit- | - | +/- 1% | TH00S020QCM21CP520 | CCI-DAT-1460 | PO# 4500189704 | PRO-PID-30 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 10 | 20 | 30 | 40 | 0 | 0 | 10 | 20 | 30 | 40 | [9 empty] | NO
476 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 21CT020 | - | Rosemount 644HANAJ1M4Q4T1 | - | NO | NO | 20 | -5 to 50 | Separation Plant - Temperature | -edit- | -5 to 50 | +/- 1% | TH00S020QCM21CT020 | CCI-DAT-1466 | PO# 4500191995 | PRO-PID-30 | rev: 6.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2703 MEC-DET-1031 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -5 | 8.75 | 22.5 | 36.25 | 50 | 0 | -5 | 8.75 | 22.5 | 36.25 | 50 | [9 empty] | NO
477 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 30CL031 | - | Vega PS21.XXXXXGMHB+MBA.BB | - | NO | NO |  | 0 to 1500 | Separation Plant - Level | -edit- | 0 to 1500 | +/- 1% | TH00S020QCM30CL031 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-29 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 375 | 750 | 1125 | 1500 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
478 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 30CL032 | - | Vega PS21.XXXXXGMHB+MBA.BB | - | NO | NO |  | 0 to 1500 | Separation Plant - Level | -edit- | 0 to 1500 | +/- 1% | TH00S020QCM30CL032 | CCI-DAT-1468 | PO# 4500189544 | PRO-PID-29 | rev: 3.2 make: Vega Vendor: Instrumatics drwg: CCI-DET-2706 | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 375 | 750 | 1125 | 1500 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
479 | Tauhara B Steamfield | Separation Plant Acid Dosing System | 30CQ010 | - | E+H CLS50D-1009/0 + CYA112-1V02/0 | - | NO | NO | TBC | TBC | Separation Plant - Analyser | -edit- | TBC | +/- 1% | TH00S020QCM30CQ010 | See notes | PO# 4500191348 | PRO-PID-29 | rev: 5.6 make: E+H Vendor: EMC drwg: See notes | uS/cm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
480 | Tauhara B Steamfield | Pump Station Fire Water | 10CP401 | - | Wika 72039878+14503369 | - | NO | NO | - | 0 to 16 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00S020SGA10CP401 | CCI-DAT-1460 | PO# 4500193000 | PRO-PID-50 | rev: make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 0 | 0 | 4 | 8 | 12 | 16 | [9 empty] | NO
481 | Tauhara B Steamfield | Pump Station Fire Water | 10CP402 | - | Wika 72039878+14503369 | - | NO | NO | - | 0 to 16 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00S020SGA10CP402 | CCI-DAT-1460 | PO# 4500193000 | PRO-PID-50 | rev: make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 0 | 0 | 4 | 8 | 12 | 16 | [9 empty] | NO
482 | Tauhara B Steamfield | Pump Station Fire Water | 10CP405 | - | Wika 72039878+14503369 | - | NO | NO | - | 0 to 16 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00S020SGA10CP405 | CCI-DAT-1460 | PO# 4500193000 | PRO-PID-50 | rev: make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 0 | 0 | 4 | 8 | 12 | 16 | [9 empty] | NO
483 | Tauhara B Steamfield | Pump Station Fire Water | 10CP406 | - | Wika 72039878+14503369 | - | NO | NO | - | 0 to 16 | Pump Station - Pressure | -edit- | - | +/- 1% | TH00S020SGA10CP406 | CCI-DAT-1460 | PO# 4500193000 | PRO-PID-50 | rev: make: Wika Vendor: Wika drwg: CCI-DET-2701 | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 0 | 0 | 4 | 8 | 12 | 16 | [9 empty] | NO
484 | Tauhara B Steamfield | Separation Plant Room Temperature | 10CT001 | - | E+H TST434-J1A3B0 | - | NO | NO | - | TBC | Separation Plant - Temperature | -edit- | TBC | +/- 1% | TH00S020SAA10CT001 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 make: E+H Vendor: EMC drwg: | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | NO
485 | Tauhara B Steamfield | Separation Plant Room Temperature | 10CT002 | - | E+H TST434-J1A3B0 | - | NO | NO | - | TBC | Separation Plant - Temperature | -edit- | TBC | +/- 1% | TH00S020SAA10CT002 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 make: E+H Vendor: EMC drwg: | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | NO
486 | Tauhara B Steamfield | Separation Plant Room Temperature | 10CT003 | - | E+H TST434-J1A3B0 | - | NO | NO | - | TBC | Separation Plant - Temperature | -edit- | TBC | +/- 1% | TH00S020SAA10CT003 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 make: E+H Vendor: EMC drwg: | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | NO
487 | Tauhara B Steamfield | Pump Station Room Temperature | 10CT001 | - | E+H TST434-J1A3B0 | - | NO | NO | - | TBC | Pump Station - Temperature | -edit- | TBC | +/- 1% | TH00P020SAA10CT001 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 make: E+H Vendor: EMC drwg: | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | NO
488 | Tauhara B Steamfield | Pump Station Room Temperature | 10CT002 | - | E+H TST434-J1A3B0 | - | NO | NO | - | TBC | Pump Station - Temperature | -edit- | TBC | +/- 1% | TH00P020SAA10CT002 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 make: E+H Vendor: EMC drwg: | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | NO
489 | Tauhara B Steamfield | Pump Station Room Temperature | 10CT003 | - | E+H TST434-J1A3B0 | - | NO | NO | - | TBC | Pump Station - Temperature | -edit- | TBC | +/- 1% | TH00P020SAA10CT003 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 make: E+H Vendor: EMC drwg: | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | NO
490 | Tauhara B Steamfield | Pump Station Room Temperature | 10CT004 | - | E+H TST434-J1A3B0 | - | NO | NO | - | TBC | Pump Station - Temperature | -edit- | TBC | +/- 1% | TH00P020SAA10CT004 | CCI-DAT-1466 | PO# 4500199015 | - | rev: 6.3 make: E+H Vendor: EMC drwg: | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | -50 | -25 | 0 | 25 | 50 |  | -50 | -25 | 0 | 25 | 50 | [9 empty] | NO
491 | Tauhara B Steamfield | TH11 110VDC System - Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 150 V | TH11 110VDC System - Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH000110BTL10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | NO
492 | Tauhara B Steamfield | TH11 110VDC System - Current Battery Systems | 10CE201 | Indication | ? | C | NO | NO | - | 0 to 150 A | TH11 110VDC System - Current - - | -edit- | 0 to 150 A | +/- 1% | TH000110BTL10CE201 | - |  | - |  | Amps | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
493 | Tauhara B Steamfield | TH12 110VDC System - Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 150 V | TH12 110VDC System - Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH000120BTL10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | NO
494 | Tauhara B Steamfield | TH12 110VDC System - Current Battery Systems | 10CE201 | Indication | ? | C | NO | NO | - | 0 to 150 A | TH12 110VDC System - Current - - | -edit- | 0 to 150 A | +/- 1% | TH000120BTL10CE201 | - |  | - |  | Amps | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
495 | Tauhara B Steamfield | TH26 110VDC System - Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 150 V | TH26 110VDC System - Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH000260BTL10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | NO
496 | Tauhara B Steamfield | TH26 110VDC System - Current Battery Systems | 10CE201 | Indication | ? | C | NO | NO | - | 0 to 150 A | TH26 110VDC System - Current - - | -edit- | 0 to 150 A | +/- 1% | TH000260BTL10CE201 | - |  | - |  | Amps | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
497 | Tauhara B Steamfield | TH28 110VDC System - Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 150 V | TH28 110VDC System - Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH000280BTL10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | NO
498 | Tauhara B Steamfield | TH28 110VDC System - Current Battery Systems | 10CE201 | Indication | ? | C | NO | NO | - | 0 to 150 A | TH28 110VDC System - Current - - | -edit- | 0 to 150 A | +/- 1% | TH000280BTL10CE201 | - |  | - |  | Amps | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
499 | Tauhara B Steamfield | TH29 110VDC System - Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 150 V | TH29 110VDC System - Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH000290BTL10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | NO
500 | Tauhara B Steamfield | TH29 110VDC System - Current Battery Systems | 10CE201 | Indication | ? | C | NO | NO | - | 0 to 150 A | TH29 110VDC System - Current - - | -edit- | 0 to 150 A | +/- 1% | TH000290BTL10CE201 | - |  | - |  | Amps | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
501 | Tauhara B Steamfield | TH37 110VDC System - Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 150 V | TH37 110VDC System - Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH000370BTL10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | NO
502 | Tauhara B Steamfield | TH37 110VDC System - Current Battery Systems | 10CE201 | Indication | ? | C | NO | NO | - | 0 to 150 A | TH37 110VDC System - Current - - | -edit- | 0 to 150 A | +/- 1% | TH000370BTL10CE201 | - |  | - |  | Amps | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
503 | Tauhara B Steamfield | SGW 230VAC Inverter A Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 300 V | SGW 230VAC Inverter A Output Voltage - - | -edit- | 0 to 300 V | +/- 1% | TH00P020BRA10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 75 | 150 | 225 | 300 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 215 | [5 empty] | NO
504 | Tauhara B Steamfield | SGW 230VAC Inverter A Output Current Battery Systems | 10CE201 | Indication | ? | C | NO | NO | - | 0 to 40 A | SGW 230VAC Inverter A Output Current - - | -edit- | 0 to 40 A | +/- 1% | TH00P020BRA10CE201 | - |  | - |  | Amps | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 10 | 20 | 30 | 40 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
505 | Tauhara B Steamfield | SGW 230VAC Inverter B Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 300 V | SGW 230VAC Inverter B Output Voltage - - | -edit- | 0 to 300 V | +/- 1% | TH00P020BRB10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 75 | 150 | 225 | 300 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 215 | [5 empty] | NO
506 | Tauhara B Steamfield | SGW 230VAC Inverter B Output Current Battery Systems | 10CE201 | Indication | ? | C | NO | NO | - | 0 to 40 A | SGW 230VAC Inverter B Output Current - - | -edit- | 0 to 40 A | +/- 1% | TH00P020BRB10CE201 | - |  | - |  | Amps | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 10 | 20 | 30 | 40 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
507 | Tauhara B Steamfield | SGW 110VDC System A Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 150 V | SGW 110VDC System A Output Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH00P020BTL10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | NO
508 | Tauhara B Steamfield | SGW 110VDC System A Output current Battery Systems | 10CE201 | Indication | ? | C | NO | NO | - | 0 to 150 A | SGW 110VDC System A Output current - - | -edit- | 0 to 150 A | +/- 1% | TH00P020BTL10CE201 | - |  | - |  | Amps | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
509 | Tauhara B Steamfield | SGW 110VDC System B Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 150 V | SGW 110VDC System B Output Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH00P020BTM10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | NO
510 | Tauhara B Steamfield | SGW 110VDC System B Output current Battery Systems | 10CE201 | Indication | ? | C | NO | NO | - | 0 to 100A | SGW 110VDC System B Output current - - | -edit- | 0 to 100A | +/- 1% | TH00P020BTM10CE201 | - |  | - |  | Amps | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
511 | Tauhara B Steamfield | SP 230VAC Inverter A Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 300 V | SP 230VAC Inverter A Output Voltage - - | -edit- | 0 to 300 V | +/- 1% | TH00S020BRA10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 75 | 150 | 225 | 300 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 215 | [5 empty] | NO
512 | Tauhara B Steamfield | SP 230VAC Inverter B Output Voltage Battery Systems | 10CE201 | Alarm & Indication | ? | C | NO | NO | - | 0 to 300 V | SP 230VAC Inverter B Output Voltage - - | -edit- | 0 to 300 V | +/- 1% | TH00S020BRA10CE201 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 75 | 150 | 225 | 300 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 215 | [5 empty] | NO
513 | Tauhara B Steamfield | SP 110VDC System A Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 150 V | SP 110VDC System A Output Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH00S020BTL10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | NO
514 | Tauhara B Steamfield | SP 110VDC System B Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 150 V | SP 110VDC System B Output Voltage - - | -edit- | 0 to 150 V | +/- 1% | TH00S020BTM10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 37.5 | 75 | 112.5 | 150 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 100 | [5 empty] | NO
515 | Tauhara B Steamfield | SP 230VAC Inverter B Output Voltage Battery Systems | 10CE101 | Alarm & Indication | ? | - | NO | NO | - | 0 to 300 V | SP 230VAC Inverter B Output Voltage - - | -edit- | 0 to 300 V | +/- 1% | TH00S020BRB10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 75 | 150 | 225 | 300 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
516 | Tauhara B Steamfield | PLC Cabinet TH11 24Vdc Comms DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TH11 24Vdc Comms - - | -edit- | 0 to 50 VDC | +/- 1% | TH000110CRA10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
517 | Tauhara B Steamfield | PLC Cabinet TH11 24Vdc IO DCS Power Supplies | 10CE102 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TH11 24Vdc IO - - | -edit- | 0 to 50 VDC | +/- 1% | TH000110CRA10CE102 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
518 | Tauhara B Steamfield | PLC Cabinet TH12 24Vdc Comms DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TH12 24Vdc Comms - - | -edit- | 0 to 50 VDC | +/- 1% | TH000120CRA10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
519 | Tauhara B Steamfield | PLC Cabinet TH12 24Vdc IO DCS Power Supplies | 10CE102 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TH12 24Vdc IO - - | -edit- | 0 to 50 VDC | +/- 1% | TH000120CRA10CE102 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
520 | Tauhara B Steamfield | PLC Cabinet TH26 24Vdc Comms DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TH26 24Vdc Comms - - | -edit- | 0 to 50 VDC | +/- 1% | TH000260CRA10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
521 | Tauhara B Steamfield | PLC Cabinet TH26 24Vdc IO DCS Power Supplies | 10CE201 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TH26 24Vdc IO - - | -edit- | 0 to 50 VDC | +/- 1% | TH000260CRA10CE201 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
522 | Tauhara B Steamfield | PLC Cabinet TH28 24Vdc Comms DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TH28 24Vdc Comms - - | -edit- | 0 to 50 VDC | +/- 1% | TH000280CRA10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
523 | Tauhara B Steamfield | PLC Cabinet TH28 24Vdc IO DCS Power Supplies | 10CE201 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TH28 24Vdc IO - - | -edit- | 0 to 50 VDC | +/- 1% | TH000280CRA10CE201 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
524 | Tauhara B Steamfield | PLC Cabinet TH29 24Vdc Comms DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TH29 24Vdc Comms - - | -edit- | 0 to 50 VDC | +/- 1% | TH000290CRA10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
525 | Tauhara B Steamfield | PLC Cabinet TH29 24Vdc IO DCS Power Supplies | 10CE201 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TH29 24Vdc IO - - | -edit- | 0 to 50 VDC | +/- 1% | TH000290CRA10CE201 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
526 | Tauhara B Steamfield | PLC Cabinet TH37 24Vdc Comms DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TH37 24Vdc Comms - - | -edit- | 0 to 50 VDC | +/- 1% | TH000370CRA10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
527 | Tauhara B Steamfield | PLC Cabinet TH37 24Vdc IO DCS Power Supplies | 10CE201 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TH37 24Vdc IO - - | -edit- | 0 to 50 VDC | +/- 1% | TH000370CRA10CE201 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
528 | Tauhara B Steamfield | PLC Cabinet TAS3 24Vdc DCS Power Supplies | 10CE101 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TAS3 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
529 | Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 1 24Vdc DCS Power Supplies | 10CE102 | Alarm & Indication | ? | C | NO | NO | - | 0 to 50 VDC | PLC Cabinet TAS3 Cluster 1 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE102 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
530 | Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 2 24Vdc DCS Power Supplies | 10CE103 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | PLC Cabinet TAS3 Cluster 2 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE103 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
531 | Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 3 24Vdc DCS Power Supplies | 10CE104 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | PLC Cabinet TAS3 Cluster 3 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE104 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
532 | Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 4 24Vdc DCS Power Supplies | 10CE105 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | PLC Cabinet TAS3 Cluster 4 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE105 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
533 | Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 5 24Vdc DCS Power Supplies | 10CE106 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | PLC Cabinet TAS3 Cluster 5 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE106 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
534 | Tauhara B Steamfield | PLC Cabinet TAS3 Cluster 6 24Vdc DCS Power Supplies | 10CE107 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | PLC Cabinet TAS3 Cluster 6 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE107 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
535 | Tauhara B Steamfield | PLC Cabinet TAS3 Vibration Rack 24Vdc DCS Power Supplies | 10CE109 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | PLC Cabinet TAS3 Vibration Rack 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRA10CE109 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
536 | Tauhara B Steamfield | Server Cabinet NSP 24Vdc DCS Power Supplies | 10CE101 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | Server Cabinet NSP 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRS10CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
537 | Tauhara B Steamfield | Server Cabinet BLDG Services 24Vdc DCS Power Supplies | 10CE102 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | Server Cabinet BLDG Services 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00P020CRS10CE102 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
538 | Tauhara B Steamfield | PLC Cabinet TAS1 24Vdc DCS Power Supplies | 20CE101 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | PLC Cabinet TAS1 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00S020CRA20CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
539 | Tauhara B Steamfield | PLC Cabinet TAS2 24Vdc DCS Power Supplies | 30CE101 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | PLC Cabinet TAS2 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00S020CRA30CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
540 | Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 1 24Vdc DCS Power Supplies | 30CE102 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | PLC Cabinet TAS2 Cluster 1 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00S020CRA30CE102 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
541 | Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 2 24Vdc DCS Power Supplies | 30CE103 | Alarm & Indication | ? | - | NO | NO | - | - | PLC Cabinet TAS2 Cluster 2 24Vdc - - | -edit- | - | +/- 1% | TH00S020CRA30CE103 | - |  | - |  | - | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | NO
542 | Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 3 24Vdc DCS Power Supplies | 30CE104 | Alarm & Indication | ? | - | NO | NO | - | - | PLC Cabinet TAS2 Cluster 3 24Vdc - - | -edit- | - | +/- 1% | TH00S020CRA30CE104 | - |  | - |  | - | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | NO
543 | Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 4 24Vdc DCS Power Supplies | 30CE105 | Alarm & Indication | ? | - | NO | NO | - | - | PLC Cabinet TAS2 Cluster 4 24Vdc - - | -edit- | - | +/- 1% | TH00S020CRA30CE105 | - |  | - |  | - | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | NO
544 | Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 5 24Vdc DCS Power Supplies | 30CE106 | Alarm & Indication | ? | - | NO | NO | - | - | PLC Cabinet TAS2 Cluster 5 24Vdc - - | -edit- | - | +/- 1% | TH00S020CRA30CE106 | - |  | - |  | - | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | NO
545 | Tauhara B Steamfield | PLC Cabinet TAS2 Cluster 6 24Vdc DCS Power Supplies | 30CE107 | Alarm & Indication | ? | - | NO | NO | - | - | PLC Cabinet TAS2 Cluster 6 24Vdc - - | -edit- | - | +/- 1% | TH00S020CRA30CE107 | - |  | - |  | - | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | NO
546 | Tauhara B Steamfield | Server Cabinet NSP 24Vdc DCS Power Supplies | 20CE101 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | Server Cabinet NSP 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00S020CRS20CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
547 | Tauhara B Steamfield | Server Cabinet Build Services 24Vdc DCS Power Supplies | 40CE101 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 VDC | Server Cabinet Build Services 24Vdc - - | -edit- | 0 to 50 VDC | +/- 1% | TH00S020CRS40CE101 | - |  | - |  | Volts | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
548 | Tauhara B Steamfield | Wellpad TH28 Common Steam/Water Dump | 10CP010 | Alarm & Indication | Rosemount 2051TG2A2B21BS5B4M4Q4Q8 | - | NO | NO | 0 | -1 to 10.3 | Wellpad TH28 - Pressure | -edit- | 0 to 10 | +/- 1% | TH000280LFC10CP010 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-31 | rev: 3.7 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
549 | Tauhara B Steamfield | Wellpad LCP (LCP2-1) Separated Water | 10CP501 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad LCP (LCP2-1) - Pressure | -edit- | - | +/- 1% | TH000320NDB10CP501 | CCI-DAT-1460 |  | PRO-PID-38 |  | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
550 | Tauhara B Steamfield | Wellpad LCP (LCP2-1) Separated Water | 10CP520 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad LCP (LCP2-1) - Pressure | -edit- | - | +/- 1% | TH000320NDB10CP520 | CCI-DAT-1460 |  | PRO-PID-38 |  | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
551 | Tauhara B Steamfield | Wellpad LCP (LCP2-2) Separated Water | 10CP510 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad LCP (LCP2-2) - Pressure | -edit- | - | +/- 1% | TH000330NDB10CP510 | CCI-DAT-1460 |  | PRO-PID-38 |  | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
552 | Tauhara B Steamfield | Wellpad LCP (LCP2-2) Separated Water | 10CP520 | - | Wika 72039876+14503369+0731277 | - | NO | NO | 15 | 0 to 60 | Wellpad LCP (LCP2-2) - Pressure | -edit- | - | +/- 1% | TH000330NDB10CP520 | CCI-DAT-1460 |  | PRO-PID-38 |  | bar(g) | bar(g) | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 15 | 30 | 45 | 60 |  | 0 | 15 | 30 | 45 | 60 | [9 empty] | NO
553 | Tauhara B Steamfield | TH26 Two Phase Pipeline Production Piping | 10-CT510 | - | Wika 72039934+72039931 | - | NO | NO | 215 | 0 to 250 | TH26 Two Phase Pipeline - - | -edit- | - | +/- 1% | TH00L070NDA10-CT510 | CCI-DAT-1463 | PO# 4500189704 | PRO-PID-34 | rev: 3.2 make: Wika Vendor: Wika drwg: CCI-DET-2703 | °C | °C | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 62.5 | 125 | 187.5 | 250 |  | 0 | 62.5 | 125 | 187.5 | 250 | [9 empty] | NO
554 | Tauhara B Steamfield | SWG Pipeline to TH29 Wellpad Separated Water | 10CP011 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 15 | -1 to 55 | SWG Pipeline to TH29 Wellpad - - | -edit- | 0 to 50 | +/- 1% | TH00L210NDB10CP011 | CCI-DAT-1461 | PO# 4500191995 | PRO-PID-32 | rev: 5.6 make: Rosemount Vendor: Custom Controls drwg: CCI-DET-2700 | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 12.5 | 25 | 37.5 | 50 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
555 | Tauhara B Steamfield | Wellpad LCP Common Steam/Water Dump | 10CL010 | - | Vega PSC21.XXXXXGBHB+DIS82.IXHKIMACX | - | NO | NO | - | 0 to 6000 | Wellpad LCP - - | -edit- | 0 to 6000 | +/- 1% | TH00LCP0LFC10CL010 | CCI-DAT-1468 |  | PRO-PID-38 |  | mm | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 1500 | 3000 | 4500 | 6000 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
556 | Tauhara B Steamfield | Pump Station Raw Water | 20CP020 | - | Rosemount 2051TG3A2B21BS5B4M4Q4Q8 | - | NO | NO | 3.49 | 0 to 25 | Pump Station - - | -edit- | - | +/- 1% | TH00S020GAC20CP020 | CCI-DAT-1460 |  | PRO-PID-51 |  | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
557 | Tauhara B Steamfield | Separation Plant Production Piping | 20CR004 | - | Cosasco 3520-T10-K03005+ER-420+CI-RS-G10180 | - | NO | NO | * | * | Separation Plant - - | -edit- | * | +/- 1% | TH00S020NDA20CR004 | COSASCO Model 3500/3500HT ER-420 |  | PRO-PID-14 |  | mm/Time Unit | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | - | - | - | - | [9 empty] | NO
558 | Tauhara B Steamfield | TH11 Building Temp Building Services | 10CT010 | - | RTD PT100 | - | NO | NO | - | 0 to 100 | TH11 Building Temp - - | -edit- | - | +/- 1% | TH000110SAA10CT010 | - |  | - |  | deg C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
559 | Tauhara B Steamfield | TH12 Building Temp Building Services | 10CT010 | - | RTD PT100 | - | NO | NO | - | 0 to 100 | TH12 Building Temp - - | -edit- | - | +/- 1% | TH000120SAA10CT010 | - |  | - |  | deg C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
560 | Tauhara B Steamfield | TH26 Building Temp Building Services | 10CT010 | - | RTD PT100 | - | NO | NO | - | 0 to 100 | TH26 Building Temp - - | -edit- | - | +/- 1% | TH000260SAA10CT010 | - |  | - |  | deg C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
561 | Tauhara B Steamfield | TH28 Building Temp Building Services | 10CT010 | - | RTD PT100 | - | NO | NO | - | 0 to 100 | TH28 Building Temp - - | -edit- | - | +/- 1% | TH000280SAA10CT010 | - |  | - |  | deg C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
562 | Tauhara B Steamfield | TH29 Building Temp Building Services | 10CT010 | - | RTD PT100 | - | NO | NO | - | 0 to 100 | TH29 Building Temp - - | -edit- | - | +/- 1% | TH000290SAA10CT010 | - |  | - |  | deg C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
563 | Tauhara B Steamfield | TH37 Building Temp Building Services | 10CT010 | - | RTD PT100 | - | NO | NO | - | 0 to 100 | TH37 Building Temp - - | -edit- | - | +/- 1% | TH000370SAA10CT010 | - |  | - |  | deg C | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 25 | 50 | 75 | 100 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
564 | Tauhara B Steamfield | SIS PLC Cabinet TAS4 24Vdc System DCS Power Supplies | 40CE101 | Alarm & Indication | ? | - | NO | NO | - | 0 to 50 | SIS PLC Cabinet TAS4 24Vdc System - - | -edit- | - | +/- 1% | TH00S020CRJ40CE101 | - |  | - |  | V | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | NO
565 | Tauhara B Steamfield | SIS PLC Cabinet TAS4 Cluster 24VDC DCS Power Supplies | 40CE102 | - | ? | - | NO | NO | - | 0 to 50 | SIS PLC Cabinet TAS4 Cluster 24VDC - - | -edit- | - | +/- 1% | TH00S020CRJ40CE102 | - |  | - |  | V | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | - | - | - | - | - | [9 empty] | NO
566 | Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CF010 | Trip & Alarm & Indication | ? | - | NO | NO | - | 0 to 10 | Separation Plant - - | -edit- | 0 to 10 | +/- 1% | TH00S020GWA11CF010 | - | PO# Vendor Supplied | TABG-JEC-0-000-PRO-PID-0055 | rev: 4.9 make: Vendor Supplied Vendor: Vendor Supplied drwg: | l/m | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 2.5 | 5 | 7.5 | 10 |  | 4 | 8 | 12 | 16 | 20 |  |  |  | 8.5 | 8.7 |  | 7 |  |  | NO
567 | Tauhara B Steamfield | Acid Dosing Seal Water Flushing Circuit B Flow Acid Dosing Seal Water | 10CF020 | Trip & Alarm & Indication | ? | - | NO | NO | - | Vendor supplied | Acid Dosing Seal Water Flushing Circuit B Flow - - | -edit- | - | +/- 1% | TH00S020GWA11CF020 | - | PO# Vendor Supplied | TABG-JEC-0-000-PRO-PID-0055 | rev: 4.9 make: Vendor Supplied Vendor: Vendor Supplied drwg: | - | - | 0 | 2024-01-22 | RF & MduP | 0 | 0 | - | - | - | - | - |  | - | - | - | - | - |  |  |  | 8.5 | 8.7 |  | 7 |  |  | NO
568 | Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CP011 | - | ? | - | NO | NO | - | 0 to 25 | Separation Plant - - | -edit- | 0 to 25 | +/- 1% | TH00S020GWA10CP011 | - |  | TABG-JEC-0-000-PRO-PID-0055 |  | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
569 | Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CP012 | - | ? | - | NO | NO | - | 0 to 25 | Separation Plant - - | -edit- | 0 to 25 | +/- 1% | TH00S020GWA10CP012 | - |  | TABG-JEC-0-000-PRO-PID-0055 |  | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
570 | Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CP021 | - | ? | - | NO | NO | - | 0 to 25 | Separation Plant - - | -edit- | 0 to 25 | +/- 1% | TH00S020GWA10CP021 | - |  | TABG-JEC-0-000-PRO-PID-0055 |  | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO
571 | Tauhara B Steamfield | Separation Plant Acid Dosing Seal Water | 10CP022 | - | ? | - | NO | NO | - | 0 to 25 | Separation Plant - - | -edit- | 0 to 25 | +/- 1% | TH00S020GWA10CP022 | - |  | TABG-JEC-0-000-PRO-PID-0055 |  | bar(g) | mA | 0 | 2024-01-22 | RF & MduP | 0 | 0 | 0 | 6.25 | 12.5 | 18.75 | 25 |  | 4 | 8 | 12 | 16 | 20 | [9 empty] | NO